## bus
name | description | baseKV | type | zone
AA_I_Z_110 | Ardnacrusha_110kV | 110 | 1 | I
AA1_I_Z_110 | Ardnacrusha_110kV | 110 | 1 | I
AD_I_Z_110 | Aghada_110kV | 110 | 1 | I
AD_I_Z_220 | Aghada_220kV | 220 | 1 | I
ADM_I_Z_110 | Adamstown_110kV | 110 | 1 | I
AGH_N_Z_110 | Aghyoule_110kV | 110 | 1 | N
AGH_N_Z_33 | Aghyoule_33kV | 33 | 1 | N
AGL_I_Z_110 | Agannygal_110kV | 110 | 1 | I
AGN_I_Z_110 | Aungierstown_110kV | 110 | 1 | I
AHA_I_Z_110 | Ahane_110kV | 110 | 1 | I
AIR_N_Z_110 | Airport Road_110kV | 110 | 1 | N
AIR_N_Z_33 | Airport Road_33kV | 33 | 1 | N
ANR_I_Z_110 | Anner_110kV | 110 | 1 | I
ANT_N_Z_110 | Antrim_110kV | 110 | 1 | N
ANT_N_Z_33 | Antrim_33kV | 33 | 1 | N
ARD_I_Z_110 | Ardnagappary_110kV | 110 | 1 | I
ARI_I_T_110 | Arigna_110kV_Tee | 110 | 1 | I
ARI_I_Z_110 | Arigna_110kV | 110 | 1 | I
ARK_I_Z_110 | Arklow_110kV | 110 | 1 | I
ARK_I_Z_220 | Arklow_220kV | 220 | 1 | I
ART_I_Z_110 | Artane_110kV | 110 | 1 | I
ARV_I_Z_110 | Arva_110kV | 110 | 1 | I
ATE_I_Z_110 | Athea_110kV | 110 | 1 | I
ATH_I_Z_110 | Athlone_110kV | 110 | 1 | I
ATN_I_Z_110 | Airton_110kV | 110 | 1 | I
ATY_I_Z_110 | Athy_110kV | 110 | 1 | I
AUG_I_Z_110 | Aughinish_110kV | 110 | 1 | I
BAL_I_Z_110 | Baltrasna_110kV | 110 | 1 | I
BAN_I_Z_110 | Bandon_110kV | 110 | 1 | I
BAN_N_Z_110 | Banbridge_110kV | 110 | 1 | N
BAN_N_Z_33 | Banbridge_33kV | 33 | 1 | N
BAR_I_T_110 | Barrymore_110kV_Tee | 110 | 1 | I
BAR_I_Z_110 | Barrymore_110kV | 110 | 1 | I
BCT_I_Z_110 | Bancroft_110kV | 110 | 1 | I
BDA_I_Z_110 | Baroda_110kV | 110 | 1 | I
BDN_I_Z_110 | Ballydine_110kV | 110 | 1 | I
BEG_I_Z_110 | Ballybeg_110kV | 110 | 1 | I
BGH_I_Z_110 | Boggeragh_110kV | 110 | 1 | I
BGN_I_Z_110 | Bogtown_110kV | 110 | 1 | I
BGT_I_Z_110 | Ballyragget_110kV | 110 | 1 | I
BIN_I_Z_110 | Binbane_110kV | 110 | 1 | I
BK_I_Z_110 | Bellacorick_110kV | 110 | 1 | I
BKM_I_Z_110 | Bunkimalta_110kV | 110 | 1 | I
BKT_I_Z_110 | Bunkimalta_110kV | 110 | 1 | I
BKY_I_Z_110 | Barnakyle_110kV | 110 | 1 | I
BLA_I_Z_110 | Blackrock_110kV | 110 | 1 | I
BLC_I_Z_110 | Belcamp_110kV | 110 | 1 | I
BLC_I_Z_220 | Belcamp_220kV | 220 | 1 | I
BLI_I_Z_110 | Ballylickey_110kV | 110 | 1 | I
BLK_I_Z_110 | Blake_110kV | 110 | 1 | I
BLU_I_Z_110 | Blundelstown_110kV | 110 | 1 | I
BMA_N_Z_110 | Ballymena_110kV | 110 | 1 | N
BMA_N_Z_33 | Ballymena_33kV | 33 | 1 | N
BNH_N_Z_110 | Ballynahinch_110kV | 110 | 1 | N
BNH_N_Z_33 | Ballynahinch_33kV | 33 | 1 | N
BNM_N_Z_110 | Belfast North_110kV | 110 | 1 | N
BNM_N_Z_33 | Belfast North_33kV | 33 | 1 | N
BOG_I_Z_110 | Banoge_110kV | 110 | 1 | I
BOL_I_Z_110 | Booltiagh_110kV | 110 | 1 | I
BPS_N_Z_110 | Ballylumford Power Station_110kV | 110 | 1 | N
BPS_N_Z_275 | Ballylumford Power Station_275kV | 275 | 1 | N
BRI_I_Z_110 | Brinny_110kV | 110 | 1 | I
BRO_N_Z_110 | Brockaghboy_110kV | 110 | 1 | N
BRO_N_Z_33 | Brockaghboy_33kV | 33 | 1 | N
BRY_I_Z_110 | Barnahely_110kV | 110 | 1 | I
BTN_I_Z_220 | Bracetown_220kV | 220 | 1 | I
BUF_I_Z_110 | Buffy_110kV | 110 | 1 | I
BUT_I_Z_110 | Butlerstown_110kV | 110 | 1 | I
BVG_N_Z_110 | Ballyvallagh_110kV | 110 | 1 | N
BVK_I_Z_110 | Ballyvouskill_110kV | 110 | 1 | I
BVK_I_Z_220 | Ballyvouskill_220kV | 220 | 1 | I
BWR_I_Z_110 | Ballywater_110kV | 110 | 1 | I
BYC_N_Z_275 | Ballycronan More (Moyle)_275kV | 275 | 1 | N
BYH_I_Z_110 | Ballynahulla_110kV | 110 | 1 | I
BYH_I_Z_220 | Ballynahulla_220kV | 220 | 1 | I
CAB_I_Z_110 | Cabra_110kV | 110 | 1 | I
CAD_Y_Z_110 | #Not Solved Yet_110kV | 110 | 1 | Y
CAH_I_Z_110 | Cahir_110kV | 110 | 1 | I
CAR_N_Z_110 | Carnmoney_110kV | 110 | 1 | N
CAR_N_Z_33 | Carnmoney_33kV | 33 | 1 | N
CAS_N_Z_110 | Castlereagh_110kV | 110 | 1 | N
CAS_N_Z_275 | Castlereagh_275kV | 275 | 1 | N
CBG_I_Z_110 | Carrowbeg_110kV | 110 | 1 | I
CBL_I_Z_110 | Cloghboola_110kV | 110 | 1 | I
CBR_I_Z_110 | Castlebar_110kV | 110 | 1 | I
CBT_I_Z_110 | Castlebagot_110kV | 110 | 1 | I
CBT_I_Z_220 | Castlebagot_220kV | 220 | 1 | I
CD_I_Z_110 | Carrigadrohid_110kV | 110 | 1 | I
CDK_I_Z_110 | Castledockrill_110kV | 110 | 1 | I
CDL_I_Z_110 | Cordal_110kV | 110 | 1 | I
CDN_I_Z_110 | Carrigdangan_110kV | 110 | 1 | I
CDU_I_Z_110 | Corduff_110kV | 110 | 1 | I
CDU_I_Z_220 | Corduff_220kV | 220 | 1 | I
CDY_I_Z_110 | Corderry_110kV | 110 | 1 | I
CEN_N_Z_110 | Belfast Central_110kV | 110 | 1 | N
CEN_N_Z_33 | Belfast Central_33kV | 33 | 1 | N
CF_I_Z_110 | Cathaleen’s Fall_110kV | 110 | 1 | I
CFD_I_Z_110 | Clonfad_110kV | 110 | 1 | I
CFM_I_Z_110 | Castlefarm_110kV | 110 | 1 | I
CGL_I_Z_110 | Coomagearlah_110kV | 110 | 1 | I
CGW_I_Z_110 | Croagh West_110kV | 110 | 1 | I
CHA_I_Z_110 | Charleville_110kV | 110 | 1 | I
CHE_I_Z_110 | Cherrywood_110kV | 110 | 1 | I
CKG_I_Z_110 | Corkagh_110kV | 110 | 1 | I
CKL_Y_Z_110 | #Not Solved Yet_110kV | 110 | 1 | Y
CKM_I_Z_110 | Carrickmines_110kV | 110 | 1 | I
CKM_I_Z_220 | Carrickmines_220kV | 220 | 1 | I
CKN_I_Z_110 | Clonkeen_110kV | 110 | 1 | I
CL_I_Z_110 | Cliff_110kV | 110 | 1 | I
CLA_I_Z_110 | Clashavoon_110kV | 110 | 1 | I
CLA_I_Z_220 | Clashavoon_220kV | 220 | 1 | I
CLE_I_Z_220 | Clonee_220kV | 220 | 1 | I
CLG_I_Z_110 | Cloghran_110kV | 110 | 1 | I
CLH_I_Z_110 | Clahane_110kV | 110 | 1 | I
CLN_I_Z_110 | Cloon_110kV | 110 | 1 | I
CLO_I_Z_110 | Clogher_110kV | 110 | 1 | I
CLU_I_Z_110 | Clutterland_110kV | 110 | 1 | I
CLW_I_Z_110 | Carlow_110kV | 110 | 1 | I
CNB_I_Z_380 | Coolnabacky_380kV | 330 | 1 | I
CNB_I_Z_110 | Coolnabacky_110kV | 110 | 1 | I
CNG_I_Z_110 | Coolnanoonag_110kV | 110 | 1 | I
COL_I_Z_110 | College Park_110kV | 110 | 1 | I
COL_N_Z_110 | Coleraine_110kV | 110 | 1 | N
COL_N_Z_33 | Coleraine_33kV | 33 | 1 | N
COO_I_Z_110 | Cookstown_110kV | 110 | 1 | I
COR_I_Z_110 | Corraclassy_110kV | 110 | 1 | I
COS_I_Z_110 | Carrick-on-Shannon_110kV | 110 | 1 | I
COW_I_Z_110 | Cow Cross_110kV | 110 | 1 | I
CPK_I_Z_110 | Central Park_110kV | 110 | 1 | I
CPS_N_Z_110 | Coolkeeragh Power Station_110kV | 110 | 1 | N
CPS_N_Z_275 | Coolkeeragh Power Station_275kV | 275 | 1 | N
CPS_N_Z_33 | Coolkeeragh Power Station_33kV | 33 | 1 | N
CRA_I_Z_110 | Crane_110kV | 110 | 1 | I
CRD_I_Z_110 | Croaghonagh_110kV | 110 | 1 | I
CRE_N_Z_110 | Cregagh_110kV | 110 | 1 | N
CRE_N_Z_33 | Cregagh_33kV | 33 | 1 | N
CRG_N_Z_110 | Creagh_110kV | 110 | 1 | N
CRG_N_Z_33 | Creagh_33kV | 33 | 1 | N
CRM_I_Z_110 | Cromcastle_110kV | 110 | 1 | I
CRO_I_Z_110 | Coolroe_110kV | 110 | 1 | I
CRR_N_Z_110 | Curragha_110kV | 110 | 1 | N
CRR_N_Z_33 | Curragha_33kV | 33 | 1 | N
CSH_I_Z_110 | Cashla_110kV | 110 | 1 | I
CSH_I_Z_220 | Cashla_220kV | 220 | 1 | I
CTG_I_Z_110 | Coomataggart_110kV | 110 | 1 | I
CTN_I_Z_110 | Cauteen_110kV | 110 | 1 | I
CTY_I_Z_110 | City West_110kV | 110 | 1 | I
CUL_I_Z_110 | Cullenagh_110kV | 110 | 1 | I
CUL_I_Z_220 | Cullenagh_220kV | 220 | 1 | I
CUN_I_Z_110 | Cunghill_110kV | 110 | 1 | I
CUR_I_Z_110 | Cureeny_110kV | 110 | 1 | I
CUS_I_Z_110 | Cushaling_110kV | 110 | 1 | I
CVW_I_Z_110 | Castleview_110kV | 110 | 1 | I
DAL_I_T_110 | Dallow_110kV_Tee | 110 | 1 | I
DAL_I_Z_110 | Dallow_110kV | 110 | 1 | I
DDK_I_Z_110 | Dundalk_110kV | 110 | 1 | I
DEE_I_Z_110 | Deenes_110kV | 110 | 1 | I
DER_I_Z_110 | Derryiron_110kV | 110 | 1 | I
DEY_I_Z_110 | Derrycarney_110kV | 110 | 1 | I
DFR_I_T_110 | Dunfirth_110kV_Tee | 110 | 1 | I
DFR_I_Z_110 | Dunfirth_110kV | 110 | 1 | I
DGN_I_Z_110 | Dungarvan_110kV | 110 | 1 | I
DKL_I_Z_110 | #Not Solved Yet_110kV | 110 | 1 | I
DLT_I_Z_110 | Dalton_110kV | 110 | 1 | I
DMY_I_Z_110 | Dunmanway_110kV | 110 | 1 | I
DON_N_Z_110 | Donegall_110kV | 110 | 1 | N
DON_N_Z_33 | Donegall_33kV | 33 | 1 | N
DOO_I_Z_110 | Doon_110kV | 110 | 1 | I
DRM_I_Z_110 | Drumkeen_110kV | 110 | 1 | I
DRO_I_Z_110 | Dromada_110kV | 110 | 1 | I
DRO_N_Z_110 | Dromore_110kV | 110 | 1 | N
DRQ_N_Z_110 | Drumquin_110kV | 110 | 1 | N
DRU_I_Z_110 | Drumline_110kV | 110 | 1 | I
DRU_N_Z_110 | Drumnakelly_110kV | 110 | 1 | N
DRU_N_Z_33 | Drumnakelly_33kV | 33 | 1 | N
DRY_I_Z_110 | Drybridge_110kV | 110 | 1 | I
DSN_I_Z_220 | Dunstown_220kV | 220 | 1 | I
DSN_I_Z_380 | Dunstown_380kV | 380 | 1 | I
DTN_I_Z_110 | Dardistown_110kV | 110 | 1 | I
DUN_N_Z_110 | Dungannon_110kV | 110 | 1 | N
DUN_N_Z_33 | Dungannon_33kV | 33 | 1 | N
DYN_I_Z_110 | Derrybrien_110kV | 110 | 1 | I
EDE_N_Z_110 | Eden_110kV | 110 | 1 | N
EDE_N_Z_33 | Eden_33kV | 33 | 1 | N
ENN_I_Z_110 | Ennis_110kV | 110 | 1 | I
ENN_N_Z_110 | Enniskillen_110kV | 110 | 1 | N
ENN_N_Z_33 | Enniskillen_33kV | 33 | 1 | N
FAS_I_Z_110 | Fassaroe_110kV | 110 | 1 | I
FIN_I_Z_110 | Finglas_110kV | 110 | 1 | I
FIN_I_Z_220 | Finglas_220kV | 220 | 1 | I
FIN_N_Z_110 | Finaghy_110kV | 110 | 1 | N
FIN_N_Z_33 | Finaghy_33kV | 33 | 1 | N
FLA_I_Z_110 | Flagford_110kV | 110 | 1 | I
FLA_I_Z_220 | Flagford_220kV | 220 | 1 | I
FRS_I_Z_110 | #Not Solved Yet_110kV | 110 | 1 | I
FTT_I_Z_110 | Fortunestown_110kV | 110 | 1 | I
GAE_I_Z_110 | Glanlee_110kV | 110 | 1 | I
GAL_I_Z_110 | Galway_110kV | 110 | 1 | I
GAN_I_Z_110 | Gallanstown_110kV | 110 | 1 | I
GCA_I_Z_110 | Grange Castle_110kV | 110 | 1 | I
GGO_I_Z_220 | Glanagow_220kV | 220 | 1 | I
GGT_I_Z_110 | Garrintaggart_110kV | 110 | 1 | I
GI_I_Z_110 | Great Island_110kV | 110 | 1 | I
GI_I_Z_220 | Great Island_220kV | 220 | 1 | I
GIL_I_Z_110 | Gilra_110kV | 110 | 1 | I
GLA_I_Z_110 | Glasmore_110kV | 110 | 1 | I
GLE_I_Z_110 | Glenlara_110kV | 110 | 1 | I
GLE_N_Z_110 | Glengormley_110kV | 110 | 1 | N
GLE_N_Z_33 | Glengormley_33kV | 33 | 1 | N
GLN_I_Z_110 | Glen_110kV | 110 | 1 | I
GLR_I_Z_110 | Glenree_110kV | 110 | 1 | I
LWN_I_Z_220 | Loughtown_220kV | 220 | 1 | I
GOL_I_T_110 | Golagh_110kV_Tee | 110 | 1 | I
GOL_I_Z_110 | Golagh_110kV | 110 | 1 | I
GOR_I_Z_110 | Gorman_110kV | 110 | 1 | I
GOR_I_Z_220 | Gorman_220kV | 220 | 1 | I
GOR_N_Z_110 | Gorman_110kV | 110 | 1 | N
GOR_N_Z_33 | Gorman_33kV | 33 | 1 | N
GRA_I_Z_110 | Grange_110kV | 110 | 1 | I
GRH_I_Z_110 | Garballagh_110kV | 110 | 1 | I
GRI_I_T_110 | Griffinrath_110kV_Tee | 110 | 1 | I
GRI_I_Z_110 | Griffinrath_110kV | 110 | 1 | I
GRO_I_Z_110 | Garrow_110kV | 110 | 1 | I
GRV_I_Z_110 | Garvagh_110kV | 110 | 1 | I
GWE_I_Z_110 | Gortawee_110kV | 110 | 1 | I
HAN_N_Z_110 | Hannastown_110kV | 110 | 1 | N
HAN_N_Z_275 | Hannastown_275kV | 275 | 1 | N
HAR_I_Z_110 | Harolds Cross_110kV | 110 | 1 | I
HEU_I_Z_110 | Heuston Square_110kV | 110 | 1 | I
HN_I_Z_220 | Huntstown_220kV | 220 | 1 | I
HWN_I_Z_110 | Harristown_110kV | 110 | 1 | I
IA_I_Z_110 | Inniscarra_110kV | 110 | 1 | I
IKE_I_T_110 | Ikerrin_110kV_Tee | 110 | 1 | I
IKE_I_Z_110 | Ikerrin_110kV | 110 | 1 | I
INC_I_Z_110 | Inchicore_110kV | 110 | 1 | I
INC_I_Z_220 | Inchicore_220kV | 220 | 1 | I
ISH_I_Z_220 | Irishtown_220kV | 220 | 1 | I
KBY_I_Z_110 | Kilbarry_110kV | 110 | 1 | I
KCR_I_Z_110 | Knockacummer_110kV | 110 | 1 | I
KCY_I_Z_110 | Kilcarbery_110kV | 110 | 1 | I
KEL_N_Z_110 | Kells_110kV | 110 | 1 | N
KEL_N_Z_275 | Kells_275kV | 275 | 1 | N
KER_I_Z_110 | Knockearagh_110kV | 110 | 1 | I
KHL_I_Z_110 | Kill Hill_110kV | 110 | 1 | I
KIN_I_Z_110 | Kinnegad_110kV | 110 | 1 | I
KKY_I_Z_110 | Kilkenny_110kV | 110 | 1 | I
KLH_I_Z_110 | Knockalough_110kV | 110 | 1 | I
KLM_I_Z_110 | Kilmore_110kV | 110 | 1 | I
KLN_I_Z_110 | Killonan_110kV | 110 | 1 | I
KLN_I_Z_220 | Killonan_220kV | 220 | 1 | I
KLP_I_Z_110 | #Not Solved Yet_110kV | 110 | 1 | I
KLP_I_Z_220 | #Not Solved Yet_220kV | 220 | 1 | I
KLS_I_Z_110 | Kellis_110kV | 110 | 1 | I
KLS_I_Z_220 | Kellis_220kV | 220 | 1 | I
KMT_N_Z_110 | Killymallaght_110kV | 110 | 1 | N
KMT_N_Z_33 | Killymallaght_33kV | 33 | 1 | N
KNO_N_Z_110 | Knock_110kV | 110 | 1 | N
KNO_N_Z_33 | Knock_33kV | 33 | 1 | N
KNR_I_Z_110 | Knockanure_110kV | 110 | 1 | I
KNR_I_Z_220 | Knockanure_220kV | 220 | 1 | I
KNY_I_Z_110 | Knockranny_110kV | 110 | 1 | I
KPG_I_Z_110 | Kilpaddoge_110kV | 110 | 1 | I
KPG_I_Z_220 | Kilpaddoge_220kV | 220 | 1 | I
KPS_N_Z_275 | Kilroot Power Station_275kV | 275 | 1 | N
KRA_I_Z_110 | Knockraha_110kV | 110 | 1 | I
KRA_I_Z_220 | Knockraha_220kV | 220 | 1 | I
KSE_I_Z_110 | Kishoge_110kV | 110 | 1 | I
KTL_I_Z_110 | Kilteel_110kV | 110 | 1 | I
KTN_I_Z_110 | Killoteran_110kV | 110 | 1 | I
KUD_I_Z_110 | Kilmahud_110kV | 110 | 1 | I
KUR_I_Z_110 | Knockumber_110kV | 110 | 1 | I
KYT_I_Z_220 | Kellystown_220kV | 220 | 1 | I
LA_I_Z_110 | Lanesboro_110kV | 110 | 1 | I
LAR_N_Z_110 | Larne_110kV | 110 | 1 | N
LAR_N_Z_33 | Larne_33kV | 33 | 1 | N
LCK_I_Z_110 | Lickny_110kV | 110 | 1 | I
LET_I_Z_110 | Letterkenny_110kV | 110 | 1 | I
LGT_I_Z_110 | Lysaghtstown_110kV | 110 | 1 | I
LIB_I_Z_110 | Liberty Street_110kV | 110 | 1 | I
LIM_I_Z_110 | Limerick_110kV | 110 | 1 | I
LIM_N_Z_110 | Limavady_110kV | 110 | 1 | N
LIM_N_Z_33 | Limavady_33kV | 33 | 1 | N
LIS_I_Z_110 | Lisdrum_110kV | 110 | 1 | I
LIS_N_Z_110 | Lisburn_110kV | 110 | 1 | N
LIS_N_Z_33 | Lisburn_33kV | 33 | 1 | N
LMR_N_Z_110 | Lisaghmore_110kV | 110 | 1 | N
LMR_N_Z_33 | Lisaghmore_33kV | 33 | 1 | N
LNA_I_Z_110 | Lenalea_110kV | 110 | 1 | I
LOG_N_Z_110 | Loguestown_110kV | 110 | 1 | N
LOG_N_Z_33 | Loguestown_33kV | 33 | 1 | N
LOU_I_Z_110 | Louth_110kV | 110 | 1 | I
LOU_I_Z_220 | Louth_220kV | 220 | 1 | I
LOU_I_Z_275 | Louth_275kV | 275 | 1 | I
LPT_I_Z_220 | Longpoint_220kV | 220 | 1 | I
LSA_I_Z_110 | Lislea_110kV | 110 | 1 | I
LSA_I_T_110 | Lislea_110kV_Tee | 110 | 1 | I
LSN_I_Z_110 | Lisheen_110kV | 110 | 1 | I
LWD_I_Z_110 | Lodgewood_110kV | 110 | 1 | I
LWD_I_Z_220 | Lodgewood_220kV | 220 | 1 | I
MAC_I_Z_110 | Macroom_110kV | 110 | 1 | I
MAG_N_Z_275 | Magherafelt_275kV | 275 | 1 | N
MAL_I_Z_110 | Mallow_110kV | 110 | 1 | I
MAY_I_Z_110 | Maynooth_110kV | 110 | 1 | I
MAY_I_Z_220 | Maynooth_220kV | 220 | 1 | I
MCD_I_Z_110 | McDermott_110kV | 110 | 1 | I
MCE_I_Z_110 | Macetown_110kV | 110 | 1 | I
MEE_I_Z_110 | Meentycat_110kV | 110 | 1 | I
MEN_I_Z_110 | Monatooreen_110kV | 110 | 1 | I
MGT_I_Z_110 | Mulgeeth_110kV | 110 | 1 | I
MHL_I_Z_110 | Misery Hill_110kV | 110 | 1 | I
MID_I_Z_110 | Midleton_110kV | 110 | 1 | I
MIL_I_Z_110 | Milltown_110kV | 110 | 1 | I
MKL_N_Z_110 | Magherakeel Cluster_110kV | 110 | 1 | N
MKL_N_Z_33 | Magherakeel Cluster_33kV | 33 | 1 | N
MLC_I_Z_110 | Mountlucas_110kV | 110 | 1 | I
MLN_I_Z_110 | Mullagharlin_110kV | 110 | 1 | I
MNH_I_Z_110 | Metro North_110kV | 110 | 1 | I
MON_I_Z_110 | Monread_110kV | 110 | 1 | I
MOY_I_Z_110 | Moy_110kV | 110 | 1 | I
MP_I_Z_110 | Moneypoint_110kV | 110 | 1 | I
MP_I_Z_220 | Moneypoint_220kV | 220 | 1 | I
MP_I_Z_380 | Moneypoint_380kV | 380 | 1 | I
MR_I_Z_110 | Marina_110kV | 110 | 1 | I
MRY_I_Z_110 | Mulreavy_110kV | 110 | 1 | I
MTA_I_Z_110 | Metro Airport_110kV | 110 | 1 | I
MTH_I_Z_110 | Meath Hill_110kV | 110 | 1 | I
MTN_I_Z_110 | Moneteen_110kV | 110 | 1 | I
MUL_I_Z_110 | Mullingar_110kV | 110 | 1 | I
MUN_I_Z_110 | Mungret_110kV | 110 | 1 | I
NAN_I_Z_110 | Nangor_110kV | 110 | 1 | I
NAR_N_Z_110 | Newtownards_110kV | 110 | 1 | N
NAR_N_Z_33 | Newtownards_33kV | 33 | 1 | N
NAV_I_Z_110 | Navan_110kV | 110 | 1 | I
NBY_I_Z_110 | Newbury_110kV | 110 | 1 | I
NEN_I_Z_110 | Nenagh_110kV | 110 | 1 | I
NEW_I_Z_110 | Newbridge_110kV | 110 | 1 | I
NEW_N_Z_110 | Newry_110kV | 110 | 1 | N
NEW_N_Z_33 | Newry_33kV | 33 | 1 | N
NQS_I_Z_110 | North Quays_110kV | 110 | 1 | I
NW_I_Z_220 | North Wall_220kV | 220 | 1 | I
OBE_I_Z_110 | Oldbridge_110kV | 110 | 1 | I
OLD_I_Z_110 | Oldcourt_110kV | 110 | 1 | I
OMA_N_Z_110 | Omagh_110kV | 110 | 1 | N
OMA_N_Z_33 | Omagh_33kV | 33 | 1 | N
ONH_I_Z_110 | #Not Solved Yet_110kV | 110 | 1 | I
OST_I_Z_220 | Oldstreet_220kV | 220 | 1 | I
OST_I_Z_380 | Oldstreet_380kV | 380 | 1 | I
OUG_I_T_110 | Oughtragh_110kV_Tee | 110 | 1 | I
OUG_I_Z_110 | Oughtragh_110kV | 110 | 1 | I
PA_I_Z_110 | Pollaphuca_110kV | 110 | 1 | I
PB_I_Z_110 | Poolbeg_110kV | 110 | 1 | I
PB_I_Z_220 | Poolbeg_220kV | 220 | 1 | I
PLA_I_Z_110 | Platin_110kV | 110 | 1 | I
PLS_I_Z_110 | Portlaoise_110kV | 110 | 1 | I
POP_I_Z_110 | Poppintree_110kV | 110 | 1 | I
POT_I_Z_110 | Pottery Road_110kV | 110 | 1 | I
PPT_I_Z_110 | Philipstown_110kV | 110 | 1 | I
PRO_I_Z_220 | Prospect_220kV | 220 | 1 | I
PRT_I_Z_380 | Portan_380kV | 380 | 1 | I
PTN_I_Z_110 | Pelletstown_110kV | 110 | 1 | I
RAF_I_Z_110 | Rafef en_110kV | 110 | 1 | I
RAF_I_Z_220 | Rafef en_220kV | 220 | 1 | I
RAT_I_Z_110 | Rathkeale_110kV | 110 | 1 | I
RAT_N_Z_110 | Rathgael_110kV | 110 | 1 | N
RAT_N_Z_33 | Rathgael_33kV | 33 | 1 | N
RE_I_Z_110 | Ringsend_110kV | 110 | 1 | I
REM_I_Z_110 | Reamore_110kV | 110 | 1 | I
RIC_I_Z_110 | Richmond_110kV | 110 | 1 | I
RNW_I_Z_110 | Rinawade_110kV | 110 | 1 | I
ROP_I_Z_110 | Rosspile_110kV | 110 | 1 | I
ROS_N_Z_110 | Rosebank_110kV | 110 | 1 | N
ROS_N_Z_33 | Rosebank_33kV | 33 | 1 | N
RRU_I_Z_110 | Ratrussan_110kV | 110 | 1 | I
RSK_N_Z_110 | Rasharkin Cluster_110kV | 110 | 1 | N
RSK_N_Z_33 | Rasharkin Cluster_33kV | 33 | 1 | N
RSY_I_Z_110 | Ringaskiddy_110kV | 110 | 1 | I
RTO_I_Z_110 | Rathnaskillo_110kV | 110 | 1 | I
RYB_I_Z_110 | Ryebrook_110kV | 110 | 1 | I
SAL_I_Z_110 | Salthill_110kV | 110 | 1 | I
SBH_I_Z_110 | Snughborough_110kV | 110 | 1 | I
SCR_I_Z_110 | Screeb_110kV | 110 | 1 | I
SEE_I_Z_110 | #Not Solved Yet_110kV | 110 | 1 | I
SH_I_Z_110 | Shannonbridge_110kV | 110 | 1 | I
SH_I_Z_220 | Shannonbridge_220kV | 220 | 1 | I
SHE_I_Z_110 | Shelton Abbey_110kV | 110 | 1 | I
SHL_I_Z_220 | Shellybanks_220kV | 220 | 1 | I
SK_I_Z_110 | Sealrock_110kV | 110 | 1 | I
SKL_I_Z_110 | Shankill_110kV | 110 | 1 | I
SKY_I_Z_110 | Srahnakilly_110kV | 110 | 1 | I
SLB_I_Z_110 | Sliabh Bawn_110kV | 110 | 1 | I
SLC_I_Z_110 | Slievecallan_110kV | 110 | 1 | I
SLI_I_Z_110 | Sligo_110kV | 110 | 1 | I
SLK_N_Z_110 | Slieve Kirk_110kV | 110 | 1 | N
SNG_I_Z_110 | Singland_110kV | 110 | 1 | I
SOM_I_T_110 | Somerset_110kV_Tee | 110 | 1 | I
SOM_I_Z_110 | Somerset_110kV | 110 | 1 | I
SOR_I_Z_110 | Sorne Hill_110kV | 110 | 1 | I
SPR_N_Z_110 | Springtown_110kV | 110 | 1 | N
SPR_N_Z_33 | Springtown_33kV | 33 | 1 | N
SRA_I_Z_110 | Srananagh_110kV | 110 | 1 | I
SRA_I_Z_220 | Srananagh_220kV | 220 | 1 | I
STR_I_T_110 | Stratford_110kV_Tee | 110 | 1 | I
STR_I_Z_110 | Stratford_110kV | 110 | 1 | I
STR_N_Z_110 | Strabane_110kV | 110 | 1 | N
STR_N_Z_33 | Strabane_33kV | 33 | 1 | N
SVN_I_Z_110 | Stevenstown_110kV | 110 | 1 | I
TAN_N_Z_110 | Tandragee_110kV | 110 | 1 | N
TAN_N_Z_275 | Tandragee_275kV | 275 | 3 | N
TAW_I_Z_110 | Tawnaghmore_110kV | 110 | 1 | I
TB_I_Z_110 | Tarbert_110kV | 110 | 1 | I
TB_I_Z_220 | Tarbert_220kV | 220 | 1 | I
TBG_I_Z_110 | Trabeg_110kV | 110 | 1 | I
TBK_I_T_110 | Tullabrack_110kV_Tee | 110 | 1 | I
TBK_I_Z_110 | Tullabrack_110kV | 110 | 1 | I
TEN_I_Z_110 | Timahoe_110kV | 110 | 1 | I
TH_I_Z_220 | Turlough Hill_220kV | 220 | 1 | I
THU_I_Z_110 | Thurles_110kV | 110 | 1 | I
TIP_I_Z_110 | Tipperary_110kV | 110 | 1 | I
TIV_I_Z_110 | Tievebrack_110kV | 110 | 1 | I
TLK_I_Z_110 | Trillick_110kV | 110 | 1 | I
TMN_N_Z_110 | Tamnamore_110kV | 110 | 1 | N
TMN_N_Z_275 | Tamnamore_275kV | 275 | 1 | N
TMN_N_Z_33 | Tamnamore_33kV | 33 | 1 | N
TNY_I_Z_110 | #Not Solved Yet_110kV | 110 | 1 | I
TON_I_Z_110 | Tonroe_110kV | 110 | 1 | I
TRE_N_Z_110 | Tremoge Cluster_110kV | 110 | 1 | N
TRE_N_Z_33 | Tremoge Cluster_33kV | 33 | 1 | N
TRI_I_Z_110 | Trien_110kV | 110 | 1 | I
TRL_I_Z_110 | Tralee_110kV | 110 | 1 | I
TRN_I_Z_110 | Trinity_110kV | 110 | 1 | I
TSB_I_Z_110 | Thornsberry_110kV | 110 | 1 | I
TTU_I_Z_110 | Tullabeg_110kV | 110 | 1 | I
TYN_I_Z_220 | Tynagh_220kV | 220 | 1 | I
UGL_I_Z_110 | Uggool_110kV | 110 | 1 | I
WAR_N_Z_110 | Waringstown_110kV | 110 | 1 | N
WAR_N_Z_33 | Waringstown_33kV | 33 | 1 | N
WAT_I_Z_110 | Waterford_110kV | 110 | 1 | I
WBK_I_Z_110 | #Not Solved Yet_110kV | 110 | 1 | I
WEX_I_Z_110 | Wexford_110kV | 110 | 1 | I
WHE_I_Z_110 | #Not Solved Yet_110kV | 110 | 1 | I
WHI_I_Z_110 | Whitegate_110kV | 110 | 1 | I
WHO_I_Z_110 | Woodhouse_110kV | 110 | 1 | I
WOL_I_Z_110 | Wolfe Tone_110kV | 110 | 1 | I
WOO_I_Z_220 | Woodland_220kV | 220 | 1 | I
WOO_I_Z_260 | Woodland_260kV | 260 | 1 | I
WOO_I_Z_380 | Woodland_380kV | 380 | 1 | I

## demand
name | busname | real | stat | VOLL
AA(I)(Z)PF1 | AA_I_Z_110 | 28.6 | 1 | 7000
AGH(N)(Z)PF0.99 | AGH_N_Z_33 | 6 | 1 | 7000
AGN(I)(Z)PF0.95 | AGN_I_Z_110 | 0 | 1 | 7000
AHA(I)(Z)PF0.965 | AHA_I_Z_110 | 1.2 | 1 | 7000
AIR(N)(Z)PF0.99 | AIR_N_Z_33 | 0 | 1 | 7000
ANR(I)(Z)PF0.95 | ANR_I_Z_110 | 14 | 1 | 7000
ANT(N)(Z)PF0.98 | ANT_N_Z_33 | 12.4 | 1 | 7000
ARD(I)(Z)PF0.99 | ARD_I_Z_110 | 4.7 | 1 | 7000
ARI(I)(T)PF0.911 | ARI_I_T_110 | 0.9 | 1 | 7000
ARK(I)(Z)PF0.967 | ARK_I_Z_110 | 15.4 | 1 | 7000
ATH(I)(Z)PF0.995 | ATH_I_Z_110 | 26.7 | 1 | 7000
ATY(I)(Z)PF0.971 | ATY_I_Z_110 | 6.1 | 1 | 7000
BAG(I)PF0.95 | CLG_I_Z_110 | 0 | 1 | 7000
BAL(I)(Z)PF0.998 | BAL_I_Z_110 | 4.5 | 1 | 7000
BAN(I)(Z)PF0.993 | BAN_I_Z_110 | 2 | 1 | 7000
BAN(I)(Z)PF0.99 | BAN_I_Z_110 | 16.6 | 1 | 7000
BAN(N)(Z)PF0.958 | BAN_N_Z_33 | 10.4 | 1 | 7000
BAR(I)(T)PF0.95 | BAR_I_T_110 | 11.5 | 1 | 7000
BDA(I)(Z)PF0.982 | BDA_I_Z_110 | 5.3 | 1 | 7000
BDN(I)(Z)PF0.95 | BDN_I_Z_110 | 3.8 | 1 | 7000
BDN(I)(Z)PF0.992 | BDN_I_Z_110 | 6 | 1 | 7000
BEG(I)(Z)PF0.992 | BEG_I_Z_110 | 4.2 | 1 | 7000
BIN(I)(Z)PF0.992 | BIN_I_Z_110 | 6.2 | 1 | 7000
BK(I)(Z)PF0.998 | BK_I_Z_110 | 1.7 | 1 | 7000
BLC(I)(Z)PF0.951 | BLC_I_Z_110 | 91.2 | 1 | 7000
BLI(I)(Z)PF0.925 | BLI_I_Z_110 | 6 | 1 | 7000
BLK(I)(Z)PF0.999 | BLK_I_Z_110 | 8.3 | 1 | 7000
BMA(N)(Z)PF0.95 | BMA_N_Z_33 | 17.1 | 1 | 7000
BNH(N)(Z)PF0.99 | BNH_N_Z_33 | 16.5 | 1 | 7000
BNM(N)(Z)PF0.99 | BNM_N_Z_33 | 13.8 | 1 | 7000
BOG(I)(Z)PF0.989 | BOG_I_Z_110 | 1.9 | 1 | 7000
BRI(I)(Z)PF0.95 | BRI_I_Z_110 | 4 | 1 | 7000
BRY(I)(Z)PF0.982 | BRY_I_Z_110 | 26.6 | 1 | 7000
BUT(I)(Z)PF0.999 | BUT_I_Z_110 | 12.9 | 1 | 7000
CAH(I)(Z)PF1 | CAH_I_Z_110 | 8.3 | 1 | 7000
CAR(N)(Z)PF0.99 | CAR_N_Z_33 | 9.6 | 1 | 7000
CBG(I)(Z)PF0.996 | CBG_I_Z_110 | 8.4 | 1 | 7000
CBR(I)(Z)PF0.984 | CBR_I_Z_110 | 10.7 | 1 | 7000
CEN(N)(Z)PF0.99 | CEN_N_Z_33 | 15.2 | 1 | 7000
CF(I)(Z)PF0.999 | CF_I_Z_110 | 6.4 | 1 | 7000
CFM(I)(Z)PF0.95 | CFM_I_Z_110 | 50.8 | 1 | 7000
CHA(I)(Z)PF0.999 | CHA_I_Z_110 | 6.6 | 1 | 7000
CKM(I)(Z)PF0.998 | CKM_I_Z_110 | 128.9 | 1 | 7000
CLE(I)(Z)PF0.95 | CLE_I_Z_220 | 90.3 | 1 | 7000
CLG(I)(Z)PF0.95 | CLG_I_Z_110 | 73.2 | 1 | 7000
CLN(I)(Z)PF1 | CLN_I_Z_110 | 7.1 | 1 | 7000
CLU(I)(Z)PF0.95 | CLU_I_Z_110 | 0 | 1 | 7000
CLW(I)(Z)PF0.982 | CLW_I_Z_110 | 18.2 | 1 | 7000
COL(I)(Z)PF0.993 | COL_I_Z_110 | 15.9 | 1 | 7000
COL(N)(Z)PF0.99 | COL_N_Z_33 | 11.8 | 1 | 7000
COS(I)(Z)PF1 | COS_I_Z_110 | 8 | 1 | 7000
COW(I)(Z)PF1 | COW_I_Z_110 | 8.2 | 1 | 7000
CPS(N)(Z)PF0.99 | CPS_N_Z_33 | 10.4 | 1 | 7000
CRA(I)(Z)PF0.999 | CRA_I_Z_110 | 12 | 1 | 7000
CRE(N)(Z)PF0.99 | CRE_N_Z_33 | 19.4 | 1 | 7000
CRG(N)(Z)PF0.99 | CRG_N_Z_33 | 14.1 | 1 | 7000
CRO(I)(Z)PF1 | CRO_I_Z_110 | 4.7 | 1 | 7000
CVW(I)(Z)PF0.95 | CVW_I_Z_110 | 0 | 1 | 7000
CVW(I)(Z)PF0.992 | CVW_I_Z_110 | 14.9 | 1 | 7000
DAL(I)(T)PF0.993 | DAL_I_T_110 | 4.8 | 1 | 7000
DDK(I)(Z)PF1 | DDK_I_Z_110 | 18.3 | 1 | 7000
DFR(I)(T)PF1 | DFR_I_T_110 | 3.3 | 1 | 7000
DGN(I)(Z)PF1 | DGN_I_Z_110 | 15.1 | 1 | 7000
DLT(I)(Z)PF0.999 | DLT_I_Z_110 | 10.7 | 1 | 7000
DMY(I)(Z)PF0.983 | DMY_I_Z_110 | 10.1 | 1 | 7000
DON(N)(Z)PF0.99 | DON_N_Z_33 | 23.9 | 1 | 7000
DOO(I)(Z)PF1 | DOO_I_Z_110 | 8.9 | 1 | 7000
DRU(I)(Z)PF0.873 | DRU_I_Z_110 | 12.9 | 1 | 7000
DRU(N)(Z)PF0.99 | DRU_N_Z_33 | 24.4 | 1 | 7000
DRY(I)(Z)PF1 | DRY_I_Z_110 | 24.3 | 1 | 7000
DUN(N)(Z)PF0.99 | DUN_N_Z_33 | 26.4 | 1 | 7000
EDE(N)(Z)PF0.99 | EDE_N_Z_33 | 9.3 | 1 | 7000
ENN(I)(Z)PF0.996 | ENN_I_Z_110 | 22 | 1 | 7000
ENN(N)(Z)PF0.99 | ENN_N_Z_33 | 17.4 | 1 | 7000
FIN(N)(Z)PF0.99 | FIN_N_Z_33 | 9.4 | 1 | 7000
FIN(I)(Z)PF0.984 | FIN_I_Z_110 | 181.2 | 1 | 7000
FTT(I)(Z)PF1 | FTT_I_Z_110 | 5.1 | 1 | 7000
GAL(I)(Z)PF1 | GAL_I_Z_110 | 34.1 | 1 | 7000
GI(I)(Z)PF0.979 | GI_I_Z_110 | 5.5 | 1 | 7000
GIL(I)(Z)PF0.95 | GIL_I_Z_110 | 11.4 | 1 | 7000
GLE(I)(Z)PF0.956 | GLE_I_Z_110 | 5 | 1 | 7000
GLE(N)(Z)PF0.99 | GLE_N_Z_33 | 8.4 | 1 | 7000
GRI(I)(T)PF1 | GRI_I_T_110 | 22.5 | 1 | 7000
GWE(I)(Z)PF0.981 | GWE_I_Z_110 | 6.5 | 1 | 7000
GWE(I)(Z)PF0.95 | GWE_I_Z_110 | 22.8 | 1 | 7000
HN(I)(Z)PF0.95 | HN_I_Z_220 | 0 | 1 | 7000
IKE(I)(T)PF0.996 | IKE_I_T_110 | 9.7 | 1 | 7000
INC(I)(Z)PF0.999 | INC_I_Z_110 | 342.7 | 1 | 7000
KBY(I)(Z)PF1 | KBY_I_Z_110 | 20.3 | 1 | 7000
KCY(I)(Z)PF0.95 | KCY_I_Z_110 | 0 | 1 | 7000
KER(I)(Z)PF0.99 | KER_I_Z_110 | 15.3 | 1 | 7000
KSE(I)(Z)PF0.95 | KSE_I_Z_110 | 0 | 1 | 7000
KTL(I)(Z)PF0.998 | KTL_I_Z_110 | 9.8 | 1 | 7000
KIN(I)(Z)PF0.95 | KIN_I_Z_110 | 10.2 | 1 | 7000
KKY(I)(Z)PF1 | KKY_I_Z_110 | 18.9 | 1 | 7000
KLM(I)(Z)PF0.992 | KLM_I_Z_110 | 9.4 | 1 | 7000
KNO(N)(Z)PF0.99 | KNO_N_Z_33 | 14.7 | 1 | 7000
KTN(I)(Z)PF0.993 | KTN_I_Z_110 | 5 | 1 | 7000
KUR(I)(Z)PF0.95 | KUR_I_Z_110 | 23.7 | 1 | 7000
KYT(I)(Z)PF0.95 | KYT_I_Z_220 | 0 | 1 | 7000
LA(I)(Z)PF1 | LA_I_Z_110 | 4.6 | 1 | 7000
LAR(N)(Z)PF0.99 | LAR_N_Z_33 | 12.4 | 1 | 7000
LET(I)(Z)PF0.996 | LET_I_Z_110 | 17.9 | 1 | 7000
LIB(I)(Z)PF0.989 | LIB_I_Z_110 | 7.9 | 1 | 7000
LIM(I)(Z)PF1 | LIM_I_Z_110 | 30.1 | 1 | 7000
LIM(N)(Z)PF0.99 | LIM_N_Z_33 | 6.1 | 1 | 7000
LIS(I)(Z)PF0.992 | LIS_I_Z_110 | 9.7 | 1 | 7000
LIS(N)(Z)PF0.99 | LIS_N_Z_33 | 22.9 | 1 | 7000
LMR(N)(Z)PF0.98 | LMR_N_Z_33 | 11.4 | 1 | 7000
LOG(N)(Z)PF0.98 | LOG_N_Z_33 | 10.7 | 1 | 7000
MAC(I)(Z)PF0.96 | MAC_I_Z_110 | 7.1 | 1 | 7000
MAL(I)(Z)PF0.988 | MAL_I_Z_110 | 12.9 | 1 | 7000
MCE(I)(Z)PF0.95 | MCE_I_Z_110 | 4.6 | 1 | 7000
MHL(I)(Z)PF1 | MHL_I_Z_110 | 9.8 | 1 | 7000
MID(I)(Z)PF0.99 | MID_I_Z_110 | 21.1 | 1 | 7000
MLN(I)(Z)PF0.95 | MLN_I_Z_110 | 4.5 | 1 | 7000
MON(I)(Z)PF0.999 | MON_I_Z_110 | 4.8 | 1 | 7000
MOY(I)(Z)PF1 | MOY_I_Z_110 | 10.1 | 1 | 7000
MR(I)(Z)PF0.999 | MR_I_Z_110 | 4.7 | 1 | 7000
MTA(I)(Z)PF0.95 | MTA_I_Z_110 | 0 | 1 | 7000
MTH(I)(Z)PF0.984 | MTH_I_Z_110 | 13.5 | 1 | 7000
MNH(I)(Z)PF0.95 | MNH_I_Z_110 | 0 | 1 | 7000
MUL(I)(Z)PF0.998 | MUL_I_Z_110 | 13.1 | 1 | 7000
MUN(I)(Z)PF0.95 | MUN_I_Z_110 | 21.5 | 1 | 7000
NAR(N)(Z)PF0.99 | NAR_N_Z_33 | 11.1 | 1 | 7000
NAV(I)(Z)PF0.969 | NAV_I_Z_110 | 17.7 | 1 | 7000
NEW(I)(Z)PF1 | NEW_I_Z_110 | 13.2 | 1 | 7000
NEW(N)(Z)PF0.99 | NEW_N_Z_33 | 21.4 | 1 | 7000
NEN(I)(Z)PF0.977 | NEN_I_Z_110 | 8.2 | 1 | 7000
OBE(I)(Z)PF0.95 | OBE_I_Z_110 | 0 | 1 | 7000
OLD(I)(Z)PF0.95 | OLD_I_Z_110 | 0.3 | 1 | 7000
OMA(N)(Z)PF0.99 | OMA_N_Z_33 | 17.3 | 1 | 7000
OUG(I)(T)PF0.989 | OUG_I_T_110 | 10.6 | 1 | 7000
PLA(I)(Z)PF0.95 | PLA_I_Z_110 | 18 | 1 | 7000
PB(I)(Z)PF0.989 | PB_I_Z_110 | 74 | 1 | 7000
PLS(I)(Z)PF0.996 | PLS_I_Z_110 | 17.6 | 1 | 7000
RAT(I)(Z)PF0.997 | RAT_I_Z_110 | 9.7 | 1 | 7000
RAT(N)(Z)PF0.99 | RAT_N_Z_33 | 14.7 | 1 | 7000
RIC(I)(Z)PF0.997 | RIC_I_Z_110 | 11.9 | 1 | 7000
RNW(I)(Z)PF0.95 | RNW_I_Z_110 | 9.1 | 1 | 7000
ROS(N)(Z)PF0.99 | ROS_N_Z_33 | 9.6 | 1 | 7000
RYB(I)(Z)PF0.95 | RYB_I_Z_110 | 104.5 | 1 | 7000
SCR(I)(Z)PF0.976 | SCR_I_Z_110 | 7.7 | 1 | 7000
SHE(I)(Z)PF0.95 | SHE_I_Z_110 | 2.3 | 1 | 7000
SAL(I)(Z)PF0.997 | SAL_I_Z_110 | 14 | 1 | 7000
SKL(I)(Z)PF0.997 | SKL_I_Z_110 | 11.5 | 1 | 7000
SLI(I)(Z)PF1 | SLI_I_Z_110 | 16.6 | 1 | 7000
SNG(I)(Z)PF1 | SNG_I_Z_110 | 5.5 | 1 | 7000
SBH(I)(Z)PF0.95 | SBH_I_Z_110 | 14.3 | 1 | 7000
SOM(I)(T)PF0.998 | SOM_I_T_110 | 3.1 | 1 | 7000
SPR(N)(Z)PF0.99 | SPR_N_Z_33 | 9.5 | 1 | 7000
STR(I)(T)PF1 | STR_I_T_110 | 5.1 | 1 | 7000
STR(N)(Z)PF0.99 | STR_N_Z_33 | 13.5 | 1 | 7000
TBG(I)(Z)PF1 | TBG_I_Z_110 | 26.9 | 1 | 7000
TBK(I)(T)PF0.992 | TBK_I_T_110 | 1.9 | 1 | 7000
THU(I)(Z)PF0.99 | THU_I_Z_110 | 10.6 | 1 | 7000
TIP(I)(Z)PF0.992 | TIP_I_Z_110 | 7.2 | 1 | 7000
TLK(I)(Z)PF0.994 | TLK_I_Z_110 | 5.9 | 1 | 7000
TON(I)(Z)PF0.987 | TON_I_Z_110 | 6.1 | 1 | 7000
TRI(I)(Z)PF0.962 | TRI_I_Z_110 | 9.2 | 1 | 7000
TRL(I)(Z)PF0.997 | TRL_I_Z_110 | 15.1 | 1 | 7000
TSB(I)(Z)PF0.996 | TSB_I_Z_110 | 10.9 | 1 | 7000
WAR(N)(Z)PF0.99 | WAR_N_Z_33 | 16.7 | 1 | 7000
WAT(I)(Z)PF1 | WAT_I_Z_110 | 28.9 | 1 | 7000
WEX(I)(Z)PF1 | WEX_I_Z_110 | 20.8 | 1 | 7000
WHI(I)(Z)PF0.95 | WHI_I_Z_110 | 9 | 1 | 7000

## ts_PD
timestep | AA(I)(Z)PF1 | AGH(N)(Z)PF0.99 | AGN(I)(Z)PF0.95 | AHA(I)(Z)PF0.965 | AIR(N)(Z)PF0.99 | ANR(I)(Z)PF0.95 | ANT(N)(Z)PF0.98 | ARD(I)(Z)PF0.99 | ARI(I)(T)PF0.911 | ARK(I)(Z)PF0.967 | ATH(I)(Z)PF0.995 | ATY(I)(Z)PF0.971 | BAG(I)PF0.95 | BAL(I)(Z)PF0.998 | BAN(I)(Z)PF0.993 | BAN(I)(Z)PF0.99 | BAN(N)(Z)PF0.958 | BAR(I)(T)PF0.95 | BDA(I)(Z)PF0.982 | BDN(I)(Z)PF0.95 | BDN(I)(Z)PF0.992 | BEG(I)(Z)PF0.992 | BIN(I)(Z)PF0.992 | BK(I)(Z)PF0.998 | BLC(I)(Z)PF0.951 | BLI(I)(Z)PF0.925 | BLK(I)(Z)PF0.999 | BMA(N)(Z)PF0.95 | BNH(N)(Z)PF0.99 | BNM(N)(Z)PF0.99 | BOG(I)(Z)PF0.989 | BRI(I)(Z)PF0.95 | BRY(I)(Z)PF0.982 | BUT(I)(Z)PF0.999 | CAH(I)(Z)PF1 | CAR(N)(Z)PF0.99 | CBG(I)(Z)PF0.996 | CBR(I)(Z)PF0.984 | CEN(N)(Z)PF0.99 | CF(I)(Z)PF0.999 | CFM(I)(Z)PF0.95 | CHA(I)(Z)PF0.999 | CKM(I)(Z)PF0.998 | CLE(I)(Z)PF0.95 | CLG(I)(Z)PF0.95 | CLN(I)(Z)PF1 | CLU(I)(Z)PF0.95 | CLW(I)(Z)PF0.982 | COL(I)(Z)PF0.993 | COL(N)(Z)PF0.99 | COS(I)(Z)PF1 | COW(I)(Z)PF1 | CPS(N)(Z)PF0.99 | CRA(I)(Z)PF0.999 | CRE(N)(Z)PF0.99 | CRG(N)(Z)PF0.99 | CRO(I)(Z)PF1 | CVW(I)(Z)PF0.95 | CVW(I)(Z)PF0.992 | DAL(I)(T)PF0.993 | DDK(I)(Z)PF1 | DFR(I)(T)PF1 | DGN(I)(Z)PF1 | DLT(I)(Z)PF0.999 | DMY(I)(Z)PF0.983 | DON(N)(Z)PF0.99 | DOO(I)(Z)PF1 | DRU(I)(Z)PF0.873 | DRU(N)(Z)PF0.99 | DRY(I)(Z)PF1 | DUN(N)(Z)PF0.99 | EDE(N)(Z)PF0.99 | ENN(I)(Z)PF0.996 | ENN(N)(Z)PF0.99 | FIN(N)(Z)PF0.99 | FIN(I)(Z)PF0.984 | FTT(I)(Z)PF1 | GAL(I)(Z)PF1 | GI(I)(Z)PF0.979 | GIL(I)(Z)PF0.95 | GLE(I)(Z)PF0.956 | GLE(N)(Z)PF0.99 | GRI(I)(T)PF1 | GWE(I)(Z)PF0.981 | GWE(I)(Z)PF0.95 | HN(I)(Z)PF0.95 | IKE(I)(T)PF0.996 | INC(I)(Z)PF0.999 | KBY(I)(Z)PF1 | KCY(I)(Z)PF0.95 | KER(I)(Z)PF0.99 | KSE(I)(Z)PF0.95 | KTL(I)(Z)PF0.998 | KIN(I)(Z)PF0.95 | KKY(I)(Z)PF1 | KLM(I)(Z)PF0.992 | KNO(N)(Z)PF0.99 | KTN(I)(Z)PF0.993 | KUR(I)(Z)PF0.95 | KYT(I)(Z)PF0.95 | LA(I)(Z)PF1 | LAR(N)(Z)PF0.99 | LET(I)(Z)PF0.996 | LIB(I)(Z)PF0.989 | LIM(I)(Z)PF1 | LIM(N)(Z)PF0.99 | LIS(I)(Z)PF0.992 | LIS(N)(Z)PF0.99 | LMR(N)(Z)PF0.98 | LOG(N)(Z)PF0.98 | MAC(I)(Z)PF0.96 | MAL(I)(Z)PF0.988 | MCE(I)(Z)PF0.95 | MHL(I)(Z)PF1 | MID(I)(Z)PF0.99 | MLN(I)(Z)PF0.95 | MON(I)(Z)PF0.999 | MOY(I)(Z)PF1 | MR(I)(Z)PF0.999 | MTA(I)(Z)PF0.95 | MTH(I)(Z)PF0.984 | MNH(I)(Z)PF0.95 | MUL(I)(Z)PF0.998 | MUN(I)(Z)PF0.95 | NAR(N)(Z)PF0.99 | NAV(I)(Z)PF0.969 | NEW(I)(Z)PF1 | NEW(N)(Z)PF0.99 | NEN(I)(Z)PF0.977 | OBE(I)(Z)PF0.95 | OLD(I)(Z)PF0.95 | OMA(N)(Z)PF0.99 | OUG(I)(T)PF0.989 | PLA(I)(Z)PF0.95 | PB(I)(Z)PF0.989 | PLS(I)(Z)PF0.996 | RAT(I)(Z)PF0.997 | RAT(N)(Z)PF0.99 | RIC(I)(Z)PF0.997 | RNW(I)(Z)PF0.95 | ROS(N)(Z)PF0.99 | RYB(I)(Z)PF0.95 | SCR(I)(Z)PF0.976 | SHE(I)(Z)PF0.95 | SAL(I)(Z)PF0.997 | SKL(I)(Z)PF0.997 | SLI(I)(Z)PF1 | SNG(I)(Z)PF1 | SBH(I)(Z)PF0.95 | SOM(I)(T)PF0.998 | SPR(N)(Z)PF0.99 | STR(I)(T)PF1 | STR(N)(Z)PF0.99 | TBG(I)(Z)PF1 | TBK(I)(T)PF0.992 | THU(I)(Z)PF0.99 | TIP(I)(Z)PF0.992 | TLK(I)(Z)PF0.994 | TON(I)(Z)PF0.987 | TRI(I)(Z)PF0.962 | TRL(I)(Z)PF0.997 | TSB(I)(Z)PF0.996 | WAR(N)(Z)PF0.99 | WAT(I)(Z)PF1 | WEX(I)(Z)PF1 | WHI(I)(Z)PF0.95
t-1 | 28.6 | 6 | 0 | 1.2 | 0 | 14 | 12.4 | 4.7 | 0.9 | 15.4 | 26.7 | 6.1 | 0 | 4.5 | 2 | 16.6 | 10.4 | 11.5 | 5.3 | 3.8 | 6 | 4.2 | 6.2 | 1.7 | 91.2 | 6 | 8.3 | 17.1 | 16.5 | 13.8 | 1.9 | 4 | 26.6 | 12.9 | 8.3 | 9.6 | 8.4 | 10.7 | 15.2 | 6.4 | 50.8 | 6.6 | 128.9 | 90.3 | 73.2 | 7.1 | 0 | 18.2 | 15.9 | 11.8 | 8 | 8.2 | 10.4 | 12 | 19.4 | 14.1 | 4.7 | 0 | 14.9 | 4.8 | 18.3 | 3.3 | 15.1 | 10.7 | 10.1 | 23.9 | 8.9 | 12.9 | 24.4 | 24.3 | 26.4 | 9.3 | 22 | 17.4 | 9.4 | 181.2 | 5.1 | 34.1 | 5.5 | 11.4 | 5 | 8.4 | 22.5 | 6.5 | 22.8 | 0 | 9.7 | 342.7 | 20.3 | 0 | 15.3 | 0 | 9.8 | 10.2 | 18.9 | 9.4 | 14.7 | 5 | 23.7 | 0 | 4.6 | 12.4 | 17.9 | 7.9 | 30.1 | 6.1 | 9.7 | 22.9 | 11.4 | 10.7 | 7.1 | 12.9 | 4.6 | 9.8 | 21.1 | 4.5 | 4.8 | 10.1 | 4.7 | 0 | 13.5 | 0 | 13.1 | 21.5 | 11.1 | 17.7 | 13.2 | 21.4 | 8.2 | 0 | 0.3 | 17.3 | 10.6 | 18 | 74 | 17.6 | 9.7 | 14.7 | 11.9 | 9.1 | 9.6 | 104.5 | 7.7 | 2.3 | 14 | 11.5 | 16.6 | 5.5 | 14.3 | 3.1 | 9.5 | 5.1 | 13.5 | 26.9 | 1.9 | 10.6 | 7.2 | 5.9 | 6.1 | 9.2 | 15.1 | 10.9 | 16.7 | 28.9 | 20.8 | 9
Note on A2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Wind =Demand; Test SNSP

## ts_VOLL
timestep | AA(I)(Z)PF1 | AGH(N)(Z)PF0.99 | AGN(I)(Z)PF0.95 | AHA(I)(Z)PF0.965 | AIR(N)(Z)PF0.99 | ANR(I)(Z)PF0.95 | ANT(N)(Z)PF0.98 | ARD(I)(Z)PF0.99 | ARI(I)(T)PF0.911 | ARK(I)(Z)PF0.967 | ATH(I)(Z)PF0.995 | ATY(I)(Z)PF0.971 | BAG(I)PF0.95 | BAL(I)(Z)PF0.998 | BAN(I)(Z)PF0.993 | BAN(I)(Z)PF0.99 | BAN(N)(Z)PF0.958 | BAR(I)(T)PF0.95 | BDA(I)(Z)PF0.982 | BDN(I)(Z)PF0.95 | BDN(I)(Z)PF0.992 | BEG(I)(Z)PF0.992 | BIN(I)(Z)PF0.992 | BK(I)(Z)PF0.998 | BLC(I)(Z)PF0.951 | BLI(I)(Z)PF0.925 | BLK(I)(Z)PF0.999 | BMA(N)(Z)PF0.95 | BNH(N)(Z)PF0.99 | BNM(N)(Z)PF0.99 | BOG(I)(Z)PF0.989 | BRI(I)(Z)PF0.95 | BRY(I)(Z)PF0.982 | BUT(I)(Z)PF0.999 | CAH(I)(Z)PF1 | CAR(N)(Z)PF0.99 | CBG(I)(Z)PF0.996 | CBR(I)(Z)PF0.984 | CEN(N)(Z)PF0.99 | CF(I)(Z)PF0.999 | CFM(I)(Z)PF0.95 | CHA(I)(Z)PF0.999 | CKM(I)(Z)PF0.998 | CLE(I)(Z)PF0.95 | CLG(I)(Z)PF0.95 | CLN(I)(Z)PF1 | CLU(I)(Z)PF0.95 | CLW(I)(Z)PF0.982 | COL(I)(Z)PF0.993 | COL(N)(Z)PF0.99 | COS(I)(Z)PF1 | COW(I)(Z)PF1 | CPS(N)(Z)PF0.99 | CRA(I)(Z)PF0.999 | CRE(N)(Z)PF0.99 | CRG(N)(Z)PF0.99 | CRO(I)(Z)PF1 | CVW(I)(Z)PF0.95 | CVW(I)(Z)PF0.992 | DAL(I)(T)PF0.993 | DDK(I)(Z)PF1 | DFR(I)(T)PF1 | DGN(I)(Z)PF1 | DLT(I)(Z)PF0.999 | DMY(I)(Z)PF0.983 | DON(N)(Z)PF0.99 | DOO(I)(Z)PF1 | DRU(I)(Z)PF0.873 | DRU(N)(Z)PF0.99 | DRY(I)(Z)PF1 | DUN(N)(Z)PF0.99 | EDE(N)(Z)PF0.99 | ENN(I)(Z)PF0.996 | ENN(N)(Z)PF0.99 | FIN(N)(Z)PF0.99 | FIN(I)(Z)PF0.984 | FTT(I)(Z)PF1 | GAL(I)(Z)PF1 | GI(I)(Z)PF0.979 | GIL(I)(Z)PF0.95 | GLE(I)(Z)PF0.956 | GLE(N)(Z)PF0.99 | GRI(I)(T)PF1 | GWE(I)(Z)PF0.981 | GWE(I)(Z)PF0.95 | HN(I)(Z)PF0.95 | IKE(I)(T)PF0.996 | INC(I)(Z)PF0.999 | KBY(I)(Z)PF1 | KCY(I)(Z)PF0.95 | KER(I)(Z)PF0.99 | KSE(I)(Z)PF0.95 | KTL(I)(Z)PF0.998 | KIN(I)(Z)PF0.95 | KKY(I)(Z)PF1 | KLM(I)(Z)PF0.992 | KNO(N)(Z)PF0.99 | KTN(I)(Z)PF0.993 | KUR(I)(Z)PF0.95 | KYT(I)(Z)PF0.95 | LA(I)(Z)PF1 | LAR(N)(Z)PF0.99 | LET(I)(Z)PF0.996 | LIB(I)(Z)PF0.989 | LIM(I)(Z)PF1 | LIM(N)(Z)PF0.99 | LIS(I)(Z)PF0.992 | LIS(N)(Z)PF0.99 | LMR(N)(Z)PF0.98 | LOG(N)(Z)PF0.98 | MAC(I)(Z)PF0.96 | MAL(I)(Z)PF0.988 | MCE(I)(Z)PF0.95 | MHL(I)(Z)PF1 | MID(I)(Z)PF0.99 | MLN(I)(Z)PF0.95 | MON(I)(Z)PF0.999 | MOY(I)(Z)PF1 | MR(I)(Z)PF0.999 | MTA(I)(Z)PF0.95 | MTH(I)(Z)PF0.984 | MNH(I)(Z)PF0.95 | MUL(I)(Z)PF0.998 | MUN(I)(Z)PF0.95 | NAR(N)(Z)PF0.99 | NAV(I)(Z)PF0.969 | NEW(I)(Z)PF1 | NEW(N)(Z)PF0.99 | NEN(I)(Z)PF0.977 | OBE(I)(Z)PF0.95 | OLD(I)(Z)PF0.95 | OMA(N)(Z)PF0.99 | OUG(I)(T)PF0.989 | PLA(I)(Z)PF0.95 | PB(I)(Z)PF0.989 | PLS(I)(Z)PF0.996 | RAT(I)(Z)PF0.997 | RAT(N)(Z)PF0.99 | RIC(I)(Z)PF0.997 | RNW(I)(Z)PF0.95 | ROS(N)(Z)PF0.99 | RYB(I)(Z)PF0.95 | SCR(I)(Z)PF0.976 | SHE(I)(Z)PF0.95 | SAL(I)(Z)PF0.997 | SKL(I)(Z)PF0.997 | SLI(I)(Z)PF1 | SNG(I)(Z)PF1 | SBH(I)(Z)PF0.95 | SOM(I)(T)PF0.998 | SPR(N)(Z)PF0.99 | STR(I)(T)PF1 | STR(N)(Z)PF0.99 | TBG(I)(Z)PF1 | TBK(I)(T)PF0.992 | THU(I)(Z)PF0.99 | TIP(I)(Z)PF0.992 | TLK(I)(Z)PF0.994 | TON(I)(Z)PF0.987 | TRI(I)(Z)PF0.962 | TRL(I)(Z)PF0.997 | TSB(I)(Z)PF0.996 | WAR(N)(Z)PF0.99 | WAT(I)(Z)PF1 | WEX(I)(Z)PF1 | WHI(I)(Z)PF0.95
t-1 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000

## branch
name | from_busname | to_busname | stat | r | x | b | ShortTermRating | ContinousRating
AA(I)(Z)>DRU(I)(Z)_110L1 | AA_I_Z_110 | DRU_I_Z_110 | 1 | 0.027 | 0.063 | 0.006 | 123.75 | 99
AA(I)(Z)>ENN(I)(Z)_110L1 | AA_I_Z_110 | ENN_I_Z_110 | 1 | 0.048 | 0.111 | 0.012 | 123.75 | 99
AA(I)(Z)>LIM(I)(Z)_110L1 | AA_I_Z_110 | LIM_I_Z_110 | 1 | 0.007 | 0.037 | 0.012 | 222.5 | 178
AA1(I)(Z)>SNG(I)(Z)_110L1 | AA1_I_Z_110 | SNG_I_Z_110 | 1 | 0.003 | 0.017 | 0.007 | 181.25 | 145
AD(I)(Z)>AD(I)(Z)_220L1 | AD_I_Z_220 | AD_I_Z_220 | 0 | 0 | 0.001 | 0.038 | 741.25 | 593
AD(I)(Z)>GGO(I)(Z)_220L1 | AD_I_Z_220 | GGO_I_Z_220 | 1 | 0 | 0.002 | 0.104 | 670 | 536
AD(I)(Z)>KRA(I)(Z)_220L1 | AD_I_Z_220 | KRA_I_Z_220 | 1 | 0.003 | 0.022 | 0.034 | 491.25 | 393
AD(I)(Z)>KRA(I)(Z)_220L2 | AD_I_Z_220 | KRA_I_Z_220 | 1 | 0.003 | 0.022 | 0.034 | 491.25 | 393
AD(I)(Z)>LPT(I)(Z)_220L1 | AD_I_Z_220 | LPT_I_Z_220 | 1 | 0 | 0.001 | 0.0265 | 741.25 | 593
AD(I)(Z)>RAF(I)(Z)_220L1 | AD_I_Z_220 | RAF_I_Z_220 | 1 | 0.001 | 0.009 | 0.252 | 542.5 | 434
AD(I)(Z)>WHI(I)(Z)_110L1 | AD_I_Z_110 | WHI_I_Z_110 | 1 | 0.005 | 0.011 | 0.001 | 123.75 | 99
ADM(I)(Z)>GCA(I)(Z)_110L1 | ADM_I_Z_110 | GCA_I_Z_110 | 1 | 0.002 | 0.004 | 0.025 | 175 | 140
ADM(I)(Z)>INC(I)(Z)_110L1 | ADM_I_Z_110 | INC_I_Z_110 | 1 | 0.009 | 0.027 | 0.024 | 128.75 | 103
AGH(N)(Z)>ENN(N)(Z)_110L1 | AGH_N_Z_110 | ENN_N_Z_110 | 1 | 0.039 | 0.095 | 0.019 | 136.25 | 109
AGL(I)(Z)>DYN(I)(Z)_110L1 | AGL_I_Z_110 | DYN_I_Z_110 | 1 | 0.012 | 0.028 | 0.003 | 131.25 | 105
AGL(I)(Z)>ENN(I)(Z)_110L1 | AGL_I_Z_110 | ENN_I_Z_110 | 1 | 0.059 | 0.131 | 0.012 | 123.75 | 99
AGN(I)(Z)>CBT(I)(Z)_110L1 | AGN_I_Z_110 | CBT_I_Z_110 | 1 | 1e-05 | 1e-05 | 0.002 | 233.75 | 187
AGN(I)(Z)>CBT(I)(Z)_110L2 | AGN_I_Z_110 | CBT_I_Z_110 | 1 | 1e-05 | 1e-05 | 0.002 | 233.75 | 187
AGN(I)(Z)>KSE(I)(Z)_110L1 | AGN_I_Z_110 | KSE_I_Z_110 | 1 | 1e-05 | 0.002 | 0.019 | 233.75 | 187
AGL(I)(Z)>SH(I)(Z)_110L1 | AGL_I_Z_110 | SH_I_Z_110 | 1 | 0.068 | 0.157 | 0.017 | 130 | 104
AHA(I)(Z)>KLN(I)(Z)_110L1 | AHA_I_Z_110 | KLN_I_Z_110 | 1 | 0.004 | 0.012 | 0.004 | 140 | 112
ANR(I)(Z)>DOO(I)(Z)_110L1 | ANR_I_Z_110 | DOO_I_Z_110 | 1 | 0.003 | 0.007 | 0.001 | 131.25 | 105
ANT(N)(Z)>KEL(N)(Z)_110L1 | ANT_N_Z_110 | KEL_N_Z_110 | 1 | 0.012 | 0.03 | 0.003 | 102.5 | 82
ANT(N)(Z)>KEL(N)(Z)_110L2 | ANT_N_Z_110 | KEL_N_Z_110 | 1 | 0.012 | 0.03 | 0.003 | 102.5 | 82
ARD(I)(Z)>TIV(I)(Z)_110L1 | ARD_I_Z_110 | TIV_I_Z_110 | 1 | 0.054 | 0.12 | 0.011 | 131.25 | 105
ARI(I)(Z)>ARI(I)(T)_110L1 | ARI_I_Z_110 | ARI_I_T_110 | 1 | 0 | 0.001 | 0 | 131.25 | 105
ARK(I)(Z)>BEG(I)(Z)_110L1 | ARK_I_Z_110 | BEG_I_Z_110 | 1 | 0.01 | 0.079 | 0.007 | 123.75 | 99
ARK(I)(Z)>BOG(I)(Z)_110L1 | ARK_I_Z_110 | BOG_I_Z_110 | 1 | 0.021 | 0.095 | 0.01 | 222.5 | 178
ARK(I)(Z)>CKM(I)(Z)_220L1 | ARK_I_Z_220 | CKM_I_Z_220 | 1 | 0.006 | 0.046 | 0.081 | 542.5 | 434
ARK(I)(Z)>LOD(I)(Z)_220L1 | ARK_I_Z_220 | LWD_I_Z_220 | 1 | 0.005 | 0.034 | 0.051 | 542.5 | 434
ARK(I)(Z)>SHE(I)(Z)_110L1 | ARK_I_Z_110 | SHE_I_Z_110 | 1 | 0.004 | 0.008 | 0.001 | 42.5 | 34
ART(I)(Z)>FIN(I)(Z)_110L1 | ART_I_Z_110 | FIN_I_Z_110 | 1 | 0.005 | 0.01 | 0.055 | 150 | 120
ART(I)(Z)>MCD(I)(Z)_110L1 | ART_I_Z_110 | MCD_I_Z_110 | 1 | 0.003 | 0.006 | 0.03 | 150 | 120
ARV(I)(Z)>COS(I)(Z)_110L1 | ARV_I_Z_110 | COS_I_Z_110 | 1 | 0.067 | 0.148 | 0.014 | 130 | 104
ARV(I)(Z)>GWE(I)(Z)_110L1 | ARV_I_Z_110 | GWE_I_Z_110 | 1 | 0.019 | 0.099 | 0.011 | 222.5 | 178
ARV(I)(Z)>NAV(I)(Z)_110L1 | ARV_I_Z_110 | NAV_I_Z_110 | 1 | 0.041 | 0.213 | 0.023 | 222.5 | 178
ARV(I)(Z)>SKL(I)(Z)_110L1 | ARV_I_Z_110 | SKL_I_Z_110 | 1 | 0.012 | 0.06 | 0.007 | 222.5 | 178
ARV(I)(Z)>SKL(I)(Z)_110L2 | ARV_I_Z_110 | SKL_I_Z_110 | 1 | 0.015 | 0.076 | 0.01 | 222.5 | 178
ATE(I)(Z)>DRO(I)(Z)_110L1 | ATE_I_Z_110 | DRO_I_Z_110 | 1 | 0.001 | 0.006 | 0.06 | 150 | 120
ATE(I)(Z)>KNR(I)(Z)_110L1 | ATE_I_Z_110 | KNR_I_Z_110 | 1 | 0.004 | 0.021 | 0.007 | 222.5 | 178
ATH(I)(Z)>LA(I)(Z)_110L1 | ATH_I_Z_110 | LA_I_Z_110 | 1 | 0.054 | 0.123 | 0.012 | 123.75 | 99
ATH(I)(Z)>SH(I)(Z)_110L1 | ATH_I_Z_110 | SH_I_Z_110 | 1 | 0.014 | 0.07 | 0.011 | 222.5 | 178
ATN(I)(Z)>INC(I)(Z)_110L1 | ATN_I_Z_110 | INC_I_Z_110 | 1 | 0.005 | 0.01 | 0.065 | 175 | 140
ATN(I)(Z)>INC(I)(Z)_110L2 | ATN_I_Z_110 | INC_I_Z_110 | 1 | 0.005 | 0.01 | 0.065 | 175 | 140
ATY(I)(Z)>CLW(I)(Z)_110L1 | ATY_I_Z_110 | CLW_I_Z_110 | 1 | 0.036 | 0.083 | 0.008 | 123.75 | 99
ATY(I)(Z)>CNB(I)(Z)_110L1 | ATY_I_Z_110 | CNB_I_Z_110 | 1 | 0.034 | 0.076 | 0.007 | 131.25 | 105
ATY(I)(Z)>PLS(I)(Z)_110L1 | ATY_I_Z_110 | PLS_I_Z_110 | 1 | 0.038 | 0.088 | 0.008 | 123.75 | 99
AUG(I)(Z)>CFM(I)(Z)_110L1 | AUG_I_Z_110 | CFM_I_Z_110 | 1 | 0.001 | 0.002 | 0.001 | 120 | 96
AUG(I)(Z)>CFM(I)(Z)_110L2 | AUG_I_Z_110 | CFM_I_Z_110 | 1 | 0.001 | 0.002 | 0.001 | 120 | 96
AUG(I)(Z)>KPG(I)(Z)_110L1 | AUG_I_Z_110 | KPG_I_Z_110 | 1 | 0.021 | 0.107 | 0.012 | 222.5 | 178
AUG(I)(Z)>MTN(I)(Z)_110L1 | AUG_I_Z_110 | MTN_I_Z_110 | 1 | 0.017 | 0.089 | 0.01 | 222.5 | 178
AUG(I)(Z)>SK(I)(Z)_110L1 | AUG_I_Z_110 | SK_I_Z_110 | 1 | 0.001 | 0.001 | 0.006 | 150 | 120
AUG(I)(Z)>SK(I)(Z)_110L2 | AUG_I_Z_110 | SK_I_Z_110 | 1 | 0.001 | 0.001 | 0.006 | 150 | 120
BAL(I)(Z)>CDU(I)(Z)_110L1 | BAL_I_Z_110 | CDU_I_Z_110 | 1 | 0.011 | 0.055 | 0.006 | 222.5 | 178
BAL(I)(Z)>DRY(I)(Z)_110L1 | BAL_I_Z_110 | DRY_I_Z_110 | 1 | 0.013 | 0.065 | 0.007 | 222.5 | 178
BAL(I)(Z)>DEE(I)(Z)_110L1 | BAL_I_Z_110 | DEE_I_Z_110 | 1 | 0.007 | 0.035 | 0.004 | 222.5 | 178
BAN(I)(Z)>BRI(I)(Z)_110L1 | BAN_I_Z_110 | BRI_I_Z_110 | 1 | 0.004 | 0.009 | 0.001 | 131.25 | 105
BAN(I)(Z)>BRI(I)(Z)_110L2 | BAN_I_Z_110 | BRI_I_Z_110 | 1 | 0.004 | 0.009 | 0.001 | 123.75 | 99
BAN(I)(Z)>DMY(I)(Z)_110L1 | BAN_I_Z_110 | DMY_I_Z_110 | 1 | 0.04 | 0.089 | 0.008 | 123.75 | 99
BAN(I)(Z)>RAF(I)(Z)_110L1 | BAN_I_Z_110 | RAF_I_Z_110 | 1 | 0.041 | 0.091 | 0.012 | 123.75 | 99
BAN(N)(Z)>TAN(N)(Z)_110L1 | BAN_N_Z_110 | TAN_N_Z_110 | 1 | 0.024 | 0.062 | 0.006 | 102.5 | 82
BAN(N)(Z)>TAN(N)(Z)_110L2 | BAN_N_Z_110 | TAN_N_Z_110 | 1 | 0.019 | 0.049 | 0.005 | 102.5 | 82
BAR(I)(Z)>BAR(I)(T)_110L1 | BAR_I_Z_110 | BAR_I_T_110 | 1 | 0 | 0.001 | 0 | 170 | 136
BCT(I)(Z)>CKM(I)(Z)_110L1 | BCT_I_Z_110 | CKM_I_Z_110 | 1 | 0.002 | 0.005 | 0.031 | 175 | 140
BCT(I)(Z)>COO(I)(Z)_110L1 | BCT_I_Z_110 | COO_I_Z_110 | 1 | 0.014 | 0.045 | 0.027 | 162.5 | 130
BDA(I)(Z)>MON(I)(Z)_110L1 | BDA_I_Z_110 | MON_I_Z_110 | 1 | 0.01 | 0.03 | 0.029 | 123.75 | 99
BDA(I)(Z)>NEW(I)(Z)_110L1 | BDA_I_Z_110 | NEW_I_Z_110 | 1 | 0.006 | 0.017 | 0.028 | 152.5 | 122
BDN(I)(Z)>CUL(I)(Z)_110L1 | BDN_I_Z_110 | CUL_I_Z_110 | 1 | 0.031 | 0.075 | 0.007 | 245 | 196
BDN(I)(Z)>DOO(I)(Z)_110L1 | BDN_I_Z_110 | DOO_I_Z_110 | 1 | 0.007 | 0.037 | 0.004 | 222.5 | 178
BEG(I)(Z)>CKM(I)(Z)_110L1 | BEG_I_Z_110 | CKM_I_Z_110 | 1 | 0.015 | 0.116 | 0.01 | 170 | 136
BGH(I)(Z)>CLA(I)(Z)_110L1 | BGH_I_Z_110 | CLA_I_Z_110 | 1 | 0.008 | 0.04 | 0.027 | 222.5 | 178
BGN(I)(Z)>MLC(I)(Z)_110L1 | BGN_I_Z_110 | MLC_I_Z_110 | 1 | 0.007 | 0.015 | 0.1 | 155 | 124
BGT(I)(Z)>CNB(I)(Z)_110L1 | BGT_I_Z_110 | CNB_I_Z_110 | 1 | 0.018 | 0.091 | 0.01 | 222.5 | 178
BGT(I)(Z)>GGT(I)(Z)_110L1 | BGT_I_Z_110 | GGT_I_Z_110 | 1 | 0.009 | 0.044 | 0.005 | 222.5 | 178
BGT(I)(Z)>KKY(I)(Z)_110L1 | BGT_I_Z_110 | KKY_I_Z_110 | 1 | 0.014 | 0.072 | 0.008 | 222.5 | 178
BIN(I)(Z)>CF(I)(Z)_110L1 | BIN_I_Z_110 | CF_I_Z_110 | 1 | 0.053 | 0.118 | 0.011 | 123.75 | 99
BIN(I)(Z)>TIV(I)(Z)_110L1 | BIN_I_Z_110 | TIV_I_Z_110 | 1 | 0.024 | 0.077 | 0.008 | 170 | 136
BK(I)(Z)>CBR(I)(Z)_110L1 | BK_I_Z_110 | CBR_I_Z_110 | 1 | 0.053 | 0.128 | 0.014 | 243.75 | 195
BK(I)(Z)>CGW(I)(Z)_110L1 | BK_I_Z_110 | CGW_I_Z_110 | 1 | 0.002 | 0.011 | 0.001 | 222.5 | 178
BK(I)(Z)>MOY(I)(Z)_110L1 | BK_I_Z_110 | MOY_I_Z_110 | 1 | 0.017 | 0.088 | 0.01 | 222.5 | 178
BK(I)(Z)>SKY(I)(Z)_110L1 | BK_I_Z_110 | SKY_I_Z_110 | 1 | 0.001 | 0.004 | 0.044 | 240 | 192
BK(I)(Z)>SKY(I)(Z)_110L2 | BK_I_Z_110 | SKY_I_Z_110 | 1 | 0.001 | 0.004 | 0.044 | 233.75 | 187
BKT(I)(Z)>CUR(I)(Z)_110L1 | BKT_I_Z_110 | CUR_I_Z_110 | 1 | 0.004 | 0.007 | 0.072 | 150 | 120
BKY(I)(Z)>CBT(I)(Z)_110L1 | BKY_I_Z_110 | CBT_I_Z_110 | 1 | 0 | 0.001 | 0.011 | 233.75 | 187
BKY(I)(Z)>CBT(I)(Z)_110L2 | BKY_I_Z_110 | CBT_I_Z_110 | 1 | 0 | 0.001 | 0.011 | 233.75 | 187
BKY(I)(Z)>KCY(I)(Z)_110 | BKY_I_Z_110 | KCY_I_Z_110 | 1 | 0 | 0.001 | 0.008 | 233.75 | 187
BLA(I)(Z)>POT(I)(Z)_110L1 | BLA_I_Z_110 | POT_I_Z_110 | 1 | 0.002 | 0.004 | 0.092 | 148.75 | 119
BLA(I)(Z)>RE(I)(Z)_110L1 | BLA_I_Z_110 | RE_I_Z_110 | 1 | 0.003 | 0.006 | 0.136 | 148.75 | 119
BLC(I)(Z)>FIN(I)(Z)_220L1 | BLC_I_Z_220 | FIN_I_Z_220 | 1 | 0 | 0.002 | 0.332 | 712.5 | 570
BLC(I)(Z)>SHL(I)(Z)_220L1 | BLC_I_Z_220 | SHL_I_Z_220 | 1 | 0.001 | 0.003 | 0.777 | 712.5 | 570
BLC(I)(Z)>GRA(I)(Z)_110L1 | BLC_I_Z_110 | GRA_I_Z_110 | 1 | 0.0025 | 0.005 | 0.031 | 175 | 140
BLC(I)(Z)>KLM(I)(Z)_110L1 | BLC_I_Z_110 | KLM_I_Z_110 | 1 | 0.002 | 0.005 | 0.029 | 175 | 140
BLC(I)(Z)>MNH(I)(Z)_110L1 | BLC_I_Z_110 | MNH_I_Z_110 | 1 | 0.003 | 0.002 | 0.195 | 1052.5 | 842
BLI(I)(Z)>DMY(I)(Z)_110L1 | BLI_I_Z_110 | DMY_I_Z_110 | 1 | 0.043 | 0.094 | 0.01 | 131.25 | 105
BLK(I)(Z)>BLK(I)(Z)_110L1 | BLK_I_Z_110 | BLK_I_Z_110 | 0 | 0.001 | 0.002 | 0 | 170 | 136
BMA(N)(Z)>KEL(N)(Z)_110L1 | BMA_N_Z_110 | KEL_N_Z_110 | 1 | 0.013 | 0.035 | 0.003 | 136.25 | 109
BMA(N)(Z)>KEL(N)(Z)_110L2 | BMA_N_Z_110 | KEL_N_Z_110 | 1 | 0.015 | 0.04 | 0.004 | 136.25 | 109
BNH(N)(Z)>CAS(N)(Z)_110L1 | BNH_N_Z_110 | CAS_N_Z_110 | 1 | 0.028 | 0.071 | 0.007 | 102.5 | 82
BNH(N)(Z)>CAS(N)(Z)_110L2 | BNH_N_Z_110 | CAS_N_Z_110 | 1 | 0.028 | 0.071 | 0.007 | 102.5 | 82
BNM(N)(Z)>DON(N)(Z)_110L1 | BNM_N_Z_110 | DON_N_Z_110 | 1 | 0.005 | 0.005 | 0.053 | 93.75 | 75
BNM(N)(Z)>DON(N)(Z)_110L2 | BNM_N_Z_110 | DON_N_Z_110 | 1 | 0.005 | 0.005 | 0.053 | 93.75 | 75
BOG(I)(Z)>TTU(I)(Z)_110L1 | BOG_I_Z_110 | TTU_I_Z_110 | 1 | 0.009 | 0.0405 | 0.0045 | 222.5 | 178
TTU(I)(Z)>CRA(I)(Z)_110L1 | TTU_I_Z_110 | CRA_I_Z_110 | 1 | 0.009 | 0.0405 | 0.0045 | 222.5 | 178
BOL(I)(Z)>ENN(I)(Z)_110L1 | BOL_I_Z_110 | ENN_I_Z_110 | 1 | 0.016 | 0.08 | 0.009 | 222.5 | 178
BOL(I)(Z)>TBK(I)(T)_110L1 | BOL_I_Z_110 | TBK_I_T_110 | 1 | 0.012 | 0.059 | 0.006 | 222.5 | 178
BPS(N)(Z)>BVG(N)(Z)_110L1 | BPS_N_Z_110 | BVG_N_Z_110 | 1 | 0.023 | 0.058 | 0.006 | 102.5 | 82
BPS(N)(Z)>BVG(N)(Z)_110L2 | BPS_N_Z_110 | BVG_N_Z_110 | 1 | 0.023 | 0.058 | 0.006 | 102.5 | 82
BPS(N)(Z)>BYC(N)(Z)_275L1 | BPS_N_Z_275 | BYC_N_Z_275 | 1 | 0 | 0.001 | 0.002 | 887.5 | 710
BPS(N)(Z)>EDE(N)(Z)_110L1 | BPS_N_Z_110 | EDE_N_Z_110 | 1 | 0.023 | 0.054 | 0.005 | 86.25 | 69
BPS(N)(Z)>EDE(N)(Z)_110L2 | BPS_N_Z_110 | EDE_N_Z_110 | 1 | 0.023 | 0.053 | 0.005 | 87.5 | 70
BPS(N)(Z)>HAN(N)(Z)_275L1 | BPS_N_Z_275 | HAN_N_Z_275 | 1 | 0.002 | 0.019 | 0.114 | 887.5 | 710
BPS(N)(Z)>KEL(N)(Z)_275L1 | BPS_N_Z_275 | KEL_N_Z_275 | 1 | 0.002 | 0.014 | 0.089 | 887.5 | 710
BPS(N)(Z)>MAG(N)(Z)_275L1 | BPS_N_Z_275 | MAG_N_Z_275 | 1 | 0.003 | 0.027 | 0.169 | 887.5 | 710
BRO(N)(Z)>RSK(N)(Z)_110L1 | BRO_N_Z_110 | RSK_N_Z_110 | 1 | 0.01 | 0.062 | 0.02 | 180 | 144
BRY(I)(Z)>RAF(I)(Z)_110L1 | BRY_I_Z_110 | RAF_I_Z_110 | 1 | 0.003 | 0.006 | 0.001 | 78.75 | 63
BRY(I)(Z)>RAF(I)(Z)_110L2 | BRY_I_Z_110 | RAF_I_Z_110 | 1 | 0.002 | 0.006 | 0.001 | 123.75 | 99
BTN(I)(Z)>CLE(I)(Z)_220L1 | BTN_I_Z_220 | CLE_I_Z_220 | 1 | 0.0001 | 0.0004 | 0.083 | 712.5 | 570
BTN(I)(Z)>CLE(I)(Z)_220L2 | BTN_I_Z_220 | CLE_I_Z_220 | 1 | 0.0001 | 0.0004 | 0.083 | 712.5 | 570
BUT(I)(Z)>CUL(I)(Z)_110L1 | BUT_I_Z_110 | CUL_I_Z_110 | 1 | 0.008 | 0.038 | 0.013 | 222.5 | 178
BUT(I)(Z)>KTN(I)(Z)_110L1 | BUT_I_Z_110 | KTN_I_Z_110 | 1 | 0.004 | 0.01 | 0.001 | 250 | 200
BVG(N)(Z)>KEL(N)(Z)_110L1 | BVG_N_Z_110 | KEL_N_Z_110 | 1 | 0.028 | 0.073 | 0.007 | 136.25 | 109
BVG(N)(Z)>KEL(N)(Z)_110L2 | BVG_N_Z_110 | KEL_N_Z_110 | 1 | 0.027 | 0.07 | 0.007 | 136.25 | 109
BVG(N)(Z)>LAR(N)(Z)_110L1 | BVG_N_Z_110 | LAR_N_Z_110 | 1 | 0.007 | 0.023 | 0.002 | 98.75 | 79
BVG(N)(Z)>LAR(N)(Z)_110L2 | BVG_N_Z_110 | LAR_N_Z_110 | 1 | 0.007 | 0.023 | 0.002 | 98.75 | 79
BVK(I)(Z)>BYH(I)(Z)_220L1 | BVK_I_Z_220 | BYH_I_Z_220 | 1 | 0.003 | 0.0246 | 0.05 | 542.5 | 434
BVK(I)(Z)>CLA(I)(Z)_220L1 | BVK_I_Z_220 | CLA_I_Z_220 | 1 | 0.002 | 0.014 | 0.025 | 925 | 740
BVK(I)(Z)>CTG(I)(Z)_110L1 | BVK_I_Z_110 | CTG_I_Z_110 | 1 | 0.006 | 0.036 | 0.386 | 285 | 228
BWR(I)(Z)>CRA(I)(Z)_110L1 | BWR_I_Z_110 | CRA_I_Z_110 | 1 | 0.008 | 0.023 | 0.137 | 143.75 | 115
BYH(I)(Z)>CDL(I)(Z)_110L1 | BYH_I_Z_110 | CDL_I_Z_110 | 1 | 0.002 | 0.011 | 0.105 | 243.75 | 195
BYH(I)(Z)>GLE(I)(Z)_110L1 | BYH_I_Z_110 | GLE_I_Z_110 | 1 | 0.006 | 0.022 | 0.186 | 155 | 124
CAB(I)(Z)>PTN(I)(Z)_110L1 | CAB_I_Z_110 | PTN_I_Z_110 | 1 | 0.002 | 0.007 | 0.005 | 100 | 80
CAB(I)(Z)>WOL(I)(Z)_110L1 | CAB_I_Z_110 | WOL_I_Z_110 | 1 | 0.003 | 0.005 | 0.029 | 150 | 120
CAH(I)(Z)>BAR(I)(T)_110L1 | CAH_I_Z_110 | BAR_I_T_110 | 1 | 0.065 | 0.15 | 0.014 | 131.25 | 105
CAH(I)(Z)>DOO(I)(Z)_110L1 | CAH_I_Z_110 | DOO_I_Z_110 | 1 | 0.01 | 0.051 | 0.006 | 222.5 | 178
CAH(I)(Z)>KHL(I)(Z)_110L1 | CAH_I_Z_110 | KHL_I_Z_110 | 1 | 0.011 | 0.058 | 0.006 | 222.5 | 178
CAH(I)(Z)>TIP(I)(Z)_110L1 | CAH_I_Z_110 | TIP_I_Z_110 | 1 | 0.011 | 0.059 | 0.006 | 222.5 | 178
CAR(N)(Z)>CAS(N)(Z)_110L1 | CAR_N_Z_110 | CAS_N_Z_110 | 1 | 0.037 | 0.088 | 0.008 | 86.25 | 69
CAR(N)(Z)>CAS(N)(Z)_110L2 | CAR_N_Z_110 | CAS_N_Z_110 | 1 | 0.037 | 0.086 | 0.008 | 87.5 | 70
CAR(N)(Z)>EDE(N)(Z)_110L1 | CAR_N_Z_110 | EDE_N_Z_110 | 1 | 0.019 | 0.043 | 0.004 | 86.25 | 69
CAR(N)(Z)>EDE(N)(Z)_110L2 | CAR_N_Z_110 | EDE_N_Z_110 | 1 | 0.019 | 0.044 | 0.004 | 86.25 | 69
CAS(N)(Z)>CRE(N)(Z)_110L1 | CAS_N_Z_110 | CRE_N_Z_110 | 1 | 0.001 | 0.004 | 0.061 | 165 | 132
CAS(N)(Z)>CRE(N)(Z)_110L2 | CAS_N_Z_110 | CRE_N_Z_110 | 1 | 0.001 | 0.004 | 0.061 | 165 | 132
CAS(N)(Z)>HAN(N)(Z)_275L1 | CAS_N_Z_275 | HAN_N_Z_275 | 1 | 0.001 | 0.008 | 0.046 | 887.5 | 710
CAS(N)(Z)>HAN(N)(Z)_275L2 | CAS_N_Z_275 | HAN_N_Z_275 | 1 | 0.001 | 0.008 | 0.046 | 887.5 | 710
CAS(N)(Z)>KNO(N)(Z)_110L1 | CAS_N_Z_110 | KNO_N_Z_110 | 1 | 0.005 | 0.004 | 0.044 | 82.5 | 66
CAS(N)(Z)>KNO(N)(Z)_110L2 | CAS_N_Z_110 | KNO_N_Z_110 | 1 | 0.005 | 0.004 | 0.044 | 82.5 | 66
CAS(N)(Z)>KPS(N)(Z)_275L1 | CAS_N_Z_275 | KPS_N_Z_275 | 1 | 0.003 | 0.028 | 0.171 | 887.5 | 710
CAS(N)(Z)>NAR(N)(Z)_110L1 | CAS_N_Z_110 | NAR_N_Z_110 | 1 | 0.015 | 0.04 | 0.071 | 136.25 | 109
CAS(N)(Z)>NAR(N)(Z)_110L2 | CAS_N_Z_110 | NAR_N_Z_110 | 1 | 0.018 | 0.046 | 0.07 | 136.25 | 109
CAS(N)(Z)>RAT(N)(Z)_110L1 | CAS_N_Z_110 | RAT_N_Z_110 | 1 | 0.025 | 0.064 | 0.006 | 102.5 | 82
CAS(N)(Z)>RAT(N)(Z)_110L2 | CAS_N_Z_110 | RAT_N_Z_110 | 1 | 0.025 | 0.064 | 0.006 | 102.5 | 82
CAS(N)(Z)>ROS(N)(Z)_110L1 | CAS_N_Z_110 | ROS_N_Z_110 | 1 | 0.001 | 0.003 | 0.015 | 180 | 144
CAS(N)(Z)>ROS(N)(Z)_110L2 | CAS_N_Z_110 | ROS_N_Z_110 | 1 | 0.001 | 0.003 | 0.015 | 180 | 144
CAS(N)(Z)>TAN(N)(Z)_275L1 | CAS_N_Z_275 | TAN_N_Z_275 | 1 | 0.002 | 0.019 | 0.114 | 887.5 | 710
CTN(I)(Z)>KLN(I)(Z)_110L1 | CTN_I_Z_110 | KLN_I_Z_110 | 1 | 0.018 | 0.095 | 0.01 | 222.5 | 178
CBL(I)(Z)>TRI(I)(Z)_110L1 | CBL_I_Z_110 | TRI_I_Z_110 | 1 | 0.007 | 0.019 | 0.099 | 155 | 124
CBG(I)(Z)>CBR(I)(Z)_110L1 | CBG_I_Z_110 | CBR_I_Z_110 | 1 | 0.035 | 0.078 | 0.059 | 123.75 | 99
CBR(I)(Z)>CLN(I)(Z)_110L1 | CBR_I_Z_110 | CLN_I_Z_110 | 1 | 0.089 | 0.198 | 0.02 | 123.75 | 99
CBR(I)(Z)>DLT(I)(Z)_110L1 | CBR_I_Z_110 | DLT_I_Z_110 | 1 | 0.043 | 0.096 | 0.009 | 123.75 | 99
CBT(I)(Z)>INC(I)(Z)_220L1 | CBT_I_Z_220 | INC_I_Z_220 | 1 | 0.002 | 0.009 | 0.014 | 951.25 | 761
CBT(I)(Z)>KCY(I)(Z)_110L1 | CBT_I_Z_110 | KCY_I_Z_110 | 1 | 1e-05 | 0.001 | 0.008 | 233.75 | 187
CBT(I)(Z)>INC(I)(Z)_220L2 | CBT_I_Z_220 | INC_I_Z_220 | 1 | 0.002 | 0.012 | 0.02 | 951.25 | 761
CBT(I)(Z)>MAY(I)(Z)_220L1 | CBT_I_Z_220 | MAY_I_Z_220 | 1 | 0.002 | 0.012 | 0.018 | 951.25 | 761
CBT(I)(Z)>MAY(I)(Z)_220L2 | CBT_I_Z_220 | MAY_I_Z_220 | 1 | 0.002 | 0.01 | 0.016 | 951.25 | 761
CD(I)(Z)>KBY(I)(Z)_110L1 | CD_I_Z_110 | KBY_I_Z_110 | 1 | 0.02 | 0.104 | 0.025 | 222.5 | 178
CD(I)(Z)>MAC(I)(Z)_110L1 | CD_I_Z_110 | MAC_I_Z_110 | 1 | 0.002 | 0.008 | 0.001 | 222.5 | 178
CDK(I)(Z)>LWD(I)(Z)_110L1 | CDK_I_Z_110 | LWD_I_Z_110 | 1 | 0.003 | 0.009 | 0.051 | 143.75 | 115
CDU(I)(Z)>FIN(I)(Z)_220L1 | CDU_I_Z_220 | FIN_I_Z_220 | 1 | 0 | 0.003 | 0.005 | 542.5 | 434
CDU(I)(Z)>FIN(I)(Z)_220L2 | CDU_I_Z_220 | FIN_I_Z_220 | 1 | 0 | 0.003 | 0.005 | 542.5 | 434
CDU(I)(Z)>HN(I)(Z)_220L1 | CDU_I_Z_220 | HN_I_Z_220 | 1 | 0 | 0.001 | 0.134 | 693.75 | 555
CDU(I)(Z)>BLU(I)(Z)_110L1 | CDU_I_Z_110 | BLU_I_Z_110 | 1 | 0.079 | 0.191 | 0.025 | 153.75 | 123
CDU(I)(Z)>GLN(I)(Z)_110L1 | CDU_I_Z_220 | GLN_I_Z_110 | 1 | 0.007 | 0.036 | 0.004 | 222.5 | 178
BLU(I)(Z)>MUL(I)(Z)_110L1 | BLU_I_Z_110 | MUL_I_Z_110 | 1 | 0.017 | 0.056 | 0.031 | 162.5 | 130
CDU(I)(Z)>PLA(I)(Z)_110L1 | CDU_I_Z_110 | PLA_I_Z_110 | 1 | 0.023 | 0.12 | 0.013 | 222.5 | 178
CDU(I)(Z)>RYB(I)(Z)_110L1 | CDU_I_Z_110 | RYB_I_Z_110 | 1 | 0.014 | 0.043 | 0.005 | 128.75 | 103
CDU(I)(Z)>SBH(I)(Z)_110L1 | CDU_I_Z_110 | SBH_I_Z_110 | 1 | 0 | 0.003 | 0.015 | 297.5 | 238
CDU(I)(Z)>WOO(I)(Z)_220L1 | CDU_I_Z_220 | WOO_I_Z_220 | 1 | 0.002 | 0.016 | 0.023 | 542.5 | 434
CDY(I)(Z)>ARI(I)(T)_110L1 | CDY_I_Z_110 | ARI_I_T_110 | 1 | 0.009 | 0.045 | 0.005 | 222.5 | 178
CDY(I)(Z)>GRV(I)(Z)_110L1 | CDY_I_Z_110 | GRV_I_Z_110 | 1 | 0.004 | 0.019 | 0.003 | 165 | 132
CDY(I)(Z)>SRA(I)(Z)_110L1 | CDY_I_Z_110 | SRA_I_Z_110 | 1 | 0.02 | 0.044 | 0.004 | 222.5 | 178
CEN(N)(Z)>CRE(N)(Z)_110L1 | CEN_N_Z_110 | CRE_N_Z_110 | 1 | 0.001 | 0.004 | 0.03 | 180 | 144
CEN(N)(Z)>CRE(N)(Z)_110L2 | CEN_N_Z_110 | CRE_N_Z_110 | 1 | 0.001 | 0.004 | 0.03 | 180 | 144
CF(I)(Z)>CAD(Y)(Z)_110L1 | CF_I_Z_110 | CAD_Y_Z_110 | 1 | 0.001 | 0.007 | 0.061 | 175 | 140
CF(I)(Z)>CKL(Y)(Z)_110L1 | CF_I_Z_110 | CKL_Y_Z_110 | 1 | 0.002 | 0.009 | 0.077 | 175 | 140
CF(I)(Z)>CL(I)(Z)_110L1 | CF_I_Z_110 | CL_I_Z_110 | 1 | 0.006 | 0.018 | 0.002 | 170 | 136
CF(I)(Z)>CLO(I)(Z)_110L1 | CF_I_Z_110 | CLO_I_Z_110 | 1 | 0.039 | 0.088 | 0.009 | 222.5 | 178
CF(I)(Z)>CLO(I)(Z)_110L2 | CF_I_Z_110 | CLO_I_Z_110 | 1 | 0.016 | 0.088 | 0.016 | 222.5 | 178
CF(I)(Z)>COR(I)(Z)_110L1 | CF_I_Z_110 | COR_I_Z_110 | 1 | 0.039 | 0.199 | 0.022 | 222.5 | 178
CF(I)(Z)>SRA(I)(Z)_110L1 | CF_I_Z_110 | SRA_I_Z_110 | 1 | 0.065 | 0.179 | 0.021 | 245 | 196
CF(I)(Z)>SRA(I)(Z)_110L2 | CF_I_Z_110 | SRA_I_Z_110 | 1 | 0.031 | 0.16 | 0.017 | 222.5 | 178
CFD(I)(Z)>MUL(I)(Z)_110L1 | CFD_I_Z_110 | MUL_I_Z_110 | 1 | 0.012 | 0.062 | 0.007 | 222.5 | 178
CFD(I)(Z)>KIN(I)(Z)_110L1 | CFD_I_Z_110 | KIN_I_Z_110 | 1 | 0.004 | 0.022 | 0.002 | 222.5 | 178
CGL(I)(Z)>GAE(I)(Z)_110L1 | CGL_I_Z_110 | GAE_I_Z_110 | 1 | 0.001 | 0.001 | 0.011 | 162.5 | 130
CHA(I)(Z)>GLE(I)(Z)_110L1 | CHA_I_Z_110 | GLE_I_Z_110 | 1 | 0.042 | 0.096 | 0.009 | 123.75 | 99
CHA(I)(Z)>KLN(I)(Z)_110L1 | CHA_I_Z_110 | KLN_I_Z_110 | 1 | 0.039 | 0.123 | 0.013 | 170 | 136
CHA(I)(Z)>MAL(I)(Z)_110L1 | CHA_I_Z_110 | MAL_I_Z_110 | 1 | 0.014 | 0.073 | 0.008 | 222.5 | 178
CHE(I)(Z)>FAS(I)(Z)_110L1 | CHE_I_Z_110 | FAS_I_Z_110 | 1 | 0.004 | 0.008 | 0.001 | 131.25 | 105
CKG(I)(Z)>CBT(I)(Z)_110L1 | CKG_I_Z_110 | CBT_I_Z_110 | 1 | 0 | 0.001 | 0.008 | 233.75 | 187
CKG(I)(Z)>CBT(I)(Z)_110L2 | CKG_I_Z_110 | CBT_I_Z_110 | 1 | 0 | 0.001 | 0.008 | 233.75 | 187
CKG(I)(Z)>KUD(I)(Z)_110L1 | CKG_I_Z_110 | KUD_I_Z_110 | 1 | 0 | 0.001 | 0.008 | 233.75 | 187
CKM(I)(Z)>CHE(I)(Z)_110L1 | CKM_I_Z_110 | CHE_I_Z_110 | 1 | 0.004 | 0.008 | 0.03 | 131.25 | 105
CKM(I)(Z)>COO(I)(Z)_110L1 | CKM_I_Z_110 | COO_I_Z_110 | 1 | 0.013 | 0.042 | 0.06 | 162.5 | 130
CKM(I)(Z)>DSN(I)(Z)_220L1 | CKM_I_Z_220 | DSN_I_Z_220 | 1 | 0.005 | 0.036 | 0.109 | 542.5 | 434
CKM(I)(Z)>FAS(I)(Z)_110L1 | CKM_I_Z_110 | FAS_I_Z_110 | 1 | 0.005 | 0.01 | 0.001 | 131.25 | 105
CKM(I)(Z)>FAS(I)(Z)_110L2 | CKM_I_Z_110 | FAS_I_Z_110 | 1 | 0.012 | 0.026 | 0.002 | 131.25 | 105
CKM(I)(Z)>ISH(I)(Z)_220L1 | CKM_I_Z_220 | ISH_I_Z_220 | 1 | 0 | 0.005 | 0.326 | 741.25 | 593
CKM(I)(Z)>POT(I)(Z)_110L1 | CKM_I_Z_110 | POT_I_Z_110 | 1 | 0.001 | 0.003 | 0.057 | 148.75 | 119
CKN(I)(Z)>CGL(I)(Z)_110L1 | CKN_I_Z_110 | CGL_I_Z_110 | 1 | 0.004 | 0.02 | 0.003 | 222.5 | 178
CKN(I)(Z)>GRO(I)(Z)_110L1 | CKN_I_Z_110 | GRO_I_Z_110 | 1 | 0.009 | 0.008 | 0.137 | 150 | 120
CKN(I)(Z)>KER(I)(Z)_110L1 | CKN_I_Z_110 | KER_I_Z_110 | 1 | 0.013 | 0.066 | 0.007 | 222.5 | 178
CLA(I)(Z)>CKN(I)(Z)_110L1 | CLA_I_Z_110 | CKN_I_Z_110 | 1 | 0.019 | 0.096 | 0.015 | 222.5 | 178
CLA(I)(Z)>DMY(I)(Z)_110L1 | CLA_I_Z_110 | DMY_I_Z_110 | 1 | 0.024 | 0.126 | 0.015 | 222.5 | 178
CLA(I)(Z)>KRA(I)(Z)_220L1 | CLA_I_Z_220 | KRA_I_Z_220 | 1 | 0.005 | 0.037 | 0.057 | 807.5 | 646
CLA(I)(Z)>MAC(I)(Z)_110L1 | CLA_I_Z_110 | MAC_I_Z_110 | 1 | 0.004 | 0.018 | 0.002 | 201.25 | 161
CLA(I)(Z)>MAC(I)(Z)_110L2 | CLA_I_Z_110 | MAC_I_Z_110 | 1 | 0.002 | 0.01 | 0.099 | 201.25 | 161
CLE(I)(Z)>CDU(I)(Z)_220L1 | CLE_I_Z_220 | CDU_I_Z_220 | 1 | 0.001 | 0.004 | 0.007 | 542.5 | 434
CLE(I)(Z)>WOO(I)(Z)_220L1 | CLE_I_Z_220 | WOO_I_Z_220 | 1 | 0.002 | 0.012 | 0.018 | 542.5 | 434
CLG(I)(Z)>CDU(I)(Z)_110L1 | CLG_I_Z_110 | CDU_I_Z_110 | 1 | 0.001 | 0.003 | 0.028 | 233.75 | 187
CLG(I)(Z)>FIN(I)(Z)_110L1 | CLG_I_Z_110 | FIN_I_Z_110 | 1 | 0.004 | 0.011 | 0.007 | 155 | 124
CLH(I)(Z)>TRI(I)(Z)_110L1 | CLH_I_Z_110 | TRI_I_Z_110 | 1 | 0.014 | 0.031 | 0.003 | 123.75 | 99
CLH(I)(Z)>TRL(I)(Z)_110L1 | CLH_I_Z_110 | TRL_I_Z_110 | 1 | 0.02 | 0.045 | 0.013 | 131.25 | 105
CLN(I)(Z)>LA(I)(Z)_110L1 | CLN_I_Z_110 | LA_I_Z_110 | 1 | 0.095 | 0.222 | 0.021 | 78.75 | 63
CLO(I)(Z)>CF(I)(Z)_110L1 | CLO_I_Z_110 | CF_I_Z_110 | 1 | 0.011 | 0.059 | 0.006 | 222.5 | 178
CLO(I)(Z)>GOL(I)(T)_110L1 | CLO_I_Z_110 | GOL_I_T_110 | 1 | 0 | 0.001 | 0.001 | 233.75 | 187
CLO(I)(Z)>MRY(I)(Z)_110L1 | CLO_I_Z_110 | MRY_I_Z_110 | 1 | 0.002 | 0.009 | 0.09 | 170 | 136
CLU(I)(Z)>CBT(I)(Z)_110L1 | CLU_I_Z_110 | CBT_I_Z_110 | 1 | 1e-05 | 1e-05 | 0.001 | 233.75 | 187
CLU(I)(Z)>KUD(I)(Z)_110L1 | CLU_I_Z_110 | KUD_I_Z_110 | 1 | 1e-05 | 0.001 | 0.01 | 233.75 | 187
CLW(I)(Z)>KLS(I)(Z)_110L1 | CLW_I_Z_110 | KLS_I_Z_110 | 1 | 0.008 | 0.019 | 0.002 | 123.75 | 99
CLW(I)(Z)>KLS(I)(Z)_110L2 | CLW_I_Z_110 | KLS_I_Z_110 | 1 | 0.008 | 0.019 | 0.002 | 123.75 | 99
CLW(I)(Z)>STR(I)(T)_110L1 | CLW_I_Z_110 | STR_I_T_110 | 1 | 0.027 | 0.061 | 0.006 | 131.25 | 105
CNB(I)(Z)>GGT(I)(T)_110L1 | CNB_I_Z_110 | GGT_I_Z_110 | 1 | 0.009 | 0.045 | 0.005 | 222.5 | 178
CNB(I)(Z)>PLS(I)(T)_110L1 | CNB_I_Z_110 | PLS_I_Z_110 | 1 | 0.005 | 0.026 | 0.008 | 222.5 | 178
CNB(I)(Z)>MP(I)(T)_380L1 | CNB_I_Z_110 | MP_I_Z_380 | 1 | 0.003 | 0.011 | 0.858 | 1971.25 | 1577
CNB(I)(Z)>DSN(I)(T)_380L1 | CNB_I_Z_110 | DSN_I_Z_380 | 1 | 0.001 | 0.003 | 0.226 | 1971.25 | 1577
COL(I)(Z)>CDU(I)(Z)_110L1 | COL_I_Z_110 | CDU_I_Z_110 | 1 | 0.001 | 0.004 | 0.02 | 178.75 | 143
COL(I)(Z)>FIN(I)(Z)_110L1 | COL_I_Z_110 | FIN_I_Z_110 | 1 | 0.003 | 0.013 | 0.037 | 130 | 104
COL(N)(Z)>CPS(N)(Z)_110L1 | COL_N_Z_110 | CPS_N_Z_110 | 1 | 0.061 | 0.161 | 0.015 | 102.5 | 82
COL(N)(Z)>LIM(N)(Z)_110L1 | COL_N_Z_110 | LIM_N_Z_110 | 1 | 0.024 | 0.064 | 0.006 | 102.5 | 82
COL(N)(Z)>LOG(N)(Z)_110L1 | COL_N_Z_110 | LOG_N_Z_110 | 1 | 0.011 | 0.027 | 0.003 | 102.5 | 82
COL(N)(Z)>LOG(N)(Z)_110L2 | COL_N_Z_110 | LOG_N_Z_110 | 1 | 0.011 | 0.027 | 0.003 | 102.5 | 82
COL(N)(Z)>RSK(N)(Z)_110L1 | COL_N_Z_110 | RSK_N_Z_110 | 1 | 0.024 | 0.069 | 0.007 | 232.5 | 186
COO(I)(Z)>FTT(I)(Z)_110L1 | COO_I_Z_110 | FTT_I_Z_110 | 1 | 0.004 | 0.011 | 0.019 | 155 | 124
COO(I)(Z)>INC(I)(Z)_110L1 | COO_I_Z_110 | INC_I_Z_110 | 1 | 0.006 | 0.016 | 0.029 | 170 | 136
COR(I)(Z)>ENN(N)(Z)_110L1 | COR_I_Z_110 | ENN_N_Z_110 | 1 | 0.041 | 0.095 | 0.009 | 123.75 | 99
COR(I)(Z)>GWE(I)(Z)_110L1 | COR_I_Z_110 | GWE_I_Z_110 | 1 | 0.007 | 0.036 | 0.004 | 222.5 | 178
COS(I)(Z)>ARI(I)(T)_110L1 | COS_I_Z_110 | ARI_I_T_110 | 1 | 0.013 | 0.065 | 0.007 | 222.5 | 178
COS(I)(Z)>FLA(I)(Z)_110L1 | COS_I_Z_110 | FLA_I_Z_110 | 1 | 0.005 | 0.012 | 0.001 | 123.75 | 99
COS(I)(Z)>FLA(I)(Z)_110L2 | COS_I_Z_110 | FLA_I_Z_110 | 1 | 0.005 | 0.011 | 0.001 | 123.75 | 99
COW(I)(Z)>OLD(I)(Z)_110L1 | COW_I_Z_110 | OLD_I_Z_110 | 1 | 0.004 | 0.008 | 0.001 | 131.25 | 105
COW(I)(Z)>OLD(I)(Z)_110L2 | COW_I_Z_110 | OLD_I_Z_110 | 1 | 0.003 | 0.008 | 0.001 | 131.25 | 105
COW(I)(Z)>RAF(I)(Z)_110L1 | COW_I_Z_110 | RAF_I_Z_110 | 1 | 0.01 | 0.024 | 0.003 | 123.75 | 99
COW(I)(Z)>WHI(I)(Z)_110L1 | COW_I_Z_110 | WHI_I_Z_110 | 1 | 0.027 | 0.062 | 0.006 | 123.75 | 99
CPK(I)(Z)>CKM(I)(Z)_110L1 | CPK_I_Z_110 | CKM_I_Z_110 | 1 | 0.002 | 0.004 | 0.025 | 125 | 100
CPK(I)(Z)>TNY(I)(Z)_110L1 | CPK_I_Z_110 | TNY_I_Z_110 | 1 | 0.003 | 0.006 | 0.072 | 125 | 100
CPS(N)(Z)>CRD(N)(Z)_110L1 | CPS_N_Z_110 | CRD_I_Z_110 | 1 | 0.001 | 0.003 | 0.087 | 250 | 200
CPS(N)(Z)>KMT(N)(Z)_110L1 | CPS_N_Z_110 | KMT_N_Z_110 | 1 | 0.011 | 0.048 | 0.005 | 178.75 | 143
CPS(N)(Z)>LIM(N)(Z)_110L1 | CPS_N_Z_110 | LIM_N_Z_110 | 1 | 0.039 | 0.101 | 0.01 | 102.5 | 82
CPS(N)(Z)>LMR(N)(Z)_110L1 | CPS_N_Z_110 | LMR_N_Z_110 | 1 | 0.012 | 0.03 | 0.003 | 102.5 | 82
CPS(N)(Z)>LMR(N)(Z)_110L2 | CPS_N_Z_110 | LMR_N_Z_110 | 1 | 0.012 | 0.03 | 0.003 | 102.5 | 82
CPS(N)(Z)>MAG(N)(Z)_275L1 | CPS_N_Z_275 | MAG_N_Z_275 | 1 | 0.006 | 0.025 | 0.151 | 515 | 412
CPS(N)(Z)>MAG(N)(Z)_275L2 | CPS_N_Z_275 | MAG_N_Z_275 | 1 | 0.006 | 0.025 | 0.151 | 515 | 412
CPS(N)(Z)>SPR(N)(Z)_110L1 | CPS_N_Z_110 | SPR_N_Z_110 | 1 | 0.011 | 0.029 | 0.012 | 102.5 | 82
CPS(N)(Z)>SPR(N)(Z)_110L2 | CPS_N_Z_110 | SPR_N_Z_110 | 1 | 0.011 | 0.029 | 0.013 | 102.5 | 82
CPS(N)(Z)>STR(N)(Z)_110L1 | CPS_N_Z_110 | STR_N_Z_110 | 1 | 0.018 | 0.053 | 0.017 | 136.25 | 109
CRA(I)(Z)>LWD(I)(Z)_110L1 | CRA_I_Z_110 | LWD_I_Z_110 | 1 | 0.004 | 0.022 | 0.004 | 222.5 | 178
CRA(I)(Z)>WEX(I)(Z)_110L1 | CRA_I_Z_110 | WEX_I_Z_110 | 1 | 0.024 | 0.076 | 0.008 | 123.75 | 99
CRG(N)(Z)>KEL(N)(Z)_110L1 | CRG_N_Z_110 | KEL_N_Z_110 | 1 | 0.029 | 0.077 | 0.013 | 102.5 | 82
CRG(N)(Z)>TMN(N)(Z)_110L1 | CRG_N_Z_110 | TMN_N_Z_110 | 1 | 0.045 | 0.119 | 0.022 | 136.25 | 109
CRM(I)(Z)>KLM(I)(Z)_110L1 | CRM_I_Z_110 | KLM_I_Z_110 | 1 | 0.001 | 0.002 | 0.014 | 175 | 140
CRM(I)(Z)>KLM(I)(Z)_110L2 | CRM_I_Z_110 | KLM_I_Z_110 | 1 | 0.001 | 0.002 | 0.014 | 175 | 140
CRO(I)(Z)>IA(I)(Z)_110L1 | CRO_I_Z_110 | IA_I_Z_110 | 1 | 0.004 | 0.01 | 0.001 | 245 | 196
CRO(I)(Z)>KBY(I)(Z)_110L1 | CRO_I_Z_110 | KBY_I_Z_110 | 1 | 0.02 | 0.049 | 0.016 | 222.5 | 178
CSH(I)(Z)>CLN(I)(Z)_110L1 | CSH_I_Z_110 | CLN_I_Z_110 | 1 | 0.014 | 0.074 | 0.008 | 222.5 | 178
CSH(I)(Z)>DLT(I)(Z)_110L1 | CSH_I_Z_110 | DLT_I_Z_110 | 1 | 0.075 | 0.205 | 0.02 | 123.75 | 99
CSH(I)(Z)>ENN(I)(Z)_110L1 | CSH_I_Z_110 | ENN_I_Z_110 | 1 | 0.034 | 0.174 | 0.019 | 222.5 | 178
CSH(I)(Z)>FLA(I)(Z)_220L1 | CSH_I_Z_220 | FLA_I_Z_220 | 1 | 0.01 | 0.076 | 0.115 | 437.5 | 350
CSH(I)(Z)>GAL(I)(Z)_110L1 | CSH_I_Z_110 | GAL_I_Z_110 | 1 | 0.022 | 0.048 | 0.004 | 123.75 | 99
CSH(I)(Z)>GAL(I)(Z)_110L2 | CSH_I_Z_110 | GAL_I_Z_110 | 1 | 0.018 | 0.039 | 0.004 | 123.75 | 99
CSH(I)(Z)>GAL(I)(Z)_110L3 | CSH_I_Z_110 | GAL_I_Z_110 | 1 | 0.018 | 0.039 | 0.004 | 123.75 | 99
CSH(I)(Z)>PRO(I)(Z)_220L1 | CSH_I_Z_220 | PRO_I_Z_220 | 1 | 0.01 | 0.077 | 0.116 | 490 | 392
CSH(I)(Z)>SAL(I)(Z)_110L1 | CSH_I_Z_110 | SAL_I_Z_110 | 1 | 0.024 | 0.074 | 0.068 | 121.25 | 97
CSH(I)(Z)>SOM(I)(T)_110L1 | CSH_I_Z_110 | SOM_I_T_110 | 1 | 0.078 | 0.172 | 0.016 | 123.75 | 99
CSH(I)(Z)>TYN(I)(Z)_220L1 | CSH_I_Z_220 | TYN_I_Z_220 | 1 | 0.005 | 0.034 | 0.058 | 951.25 | 761
CTN(I)(Z)>TIP(I)(Z)_110L1 | CTN_I_Z_110 | TIP_I_Z_110 | 1 | 0.008 | 0.043 | 0.005 | 222.5 | 178
CTY(I)(Z)>FTT(I)(Z)_110L1 | CTY_I_Z_110 | FTT_I_Z_110 | 1 | 0.001 | 0.001 | 0.018 | 155 | 124
CTY(I)(Z)>INC(I)(Z)_110L1 | CTY_I_Z_110 | INC_I_Z_110 | 1 | 0.011 | 0.03 | 0.003 | 128.75 | 103
CUL(I)(Z)>DGN(I)(Z)_110L1 | CUL_I_Z_110 | DGN_I_Z_110 | 1 | 0.022 | 0.109 | 0.02 | 222.5 | 178
CUL(I)(Z)>GI(I)(Z)_220L1 | CUL_I_Z_220 | GI_I_Z_220 | 1 | 0.003 | 0.02 | 0.044 | 932.5 | 746
CUL(I)(Z)>KRA(I)(Z)_220L1 | CUL_I_Z_220 | KRA_I_Z_220 | 1 | 0.012 | 0.074 | 0.117 | 807.5 | 646
CUL(I)(Z)>WAT(I)(Z)_110L1 | CUL_I_Z_110 | WAT_I_Z_110 | 1 | 0.007 | 0.03 | 0.055 | 222.5 | 178
CUL(I)(Z)>RTO(I)(Z)_110L1 | CUL_I_Z_110 | RTO_I_Z_110 | 1 | 0.012 | 0.062 | 0.007 | 222.5 | 178
CUN(I)(Z)>GLR(I)(Z)_110L1 | CUN_I_Z_110 | GLR_I_Z_110 | 1 | 0.039 | 0.09 | 0.009 | 222.5 | 178
CUN(I)(Z)>SLI(I)(Z)_110L1 | CUN_I_Z_110 | SLI_I_Z_110 | 1 | 0.03 | 0.073 | 0.007 | 222.5 | 178
CUR(I)(Z)>BKM(I)(Z)_110L1 | CUR_I_Z_110 | BKM_I_Z_110 | 1 | 0.004 | 0.019 | 0.192 | 237.5 | 190
CUR(I)(Z)>NEN(I)(Z)_110L1 | CUR_I_Z_110 | NEN_I_Z_110 | 1 | 0.029 | 0.065 | 0.006 | 131.25 | 105
CUS(I)(Z)>MLC(I)(Z)_110L1 | CUS_I_Z_110 | MLC_I_Z_110 | 1 | 0.015 | 0.048 | 0.005 | 170 | 136
CUS(I)(Z)>NEW(I)(Z)_110L1 | CUS_I_Z_110 | NEW_I_Z_110 | 1 | 0.026 | 0.082 | 0.008 | 167.5 | 134
CUS(I)(Z)>PLS(I)(Z)_110L1 | CUS_I_Z_110 | PLS_I_Z_110 | 1 | 0.044 | 0.14 | 0.014 | 170 | 136
CUS(I)(Z)>PPT(I)(Z)_110L1 | CUS_I_Z_110 | PPT_I_Z_110 | 1 | 0.001 | 0.005 | 0.011 | 170 | 136
CVW(I)(Z)>COW(I)(Z)_110L1 | CVW_I_Z_110 | COW_I_Z_110 | 1 | 0.025 | 0.054 | 0.018 | 123.75 | 99
CVW(I)(Z)>DKL(I)(Z)_110L1 | CVW_I_Z_110 | DKL_I_Z_110 | 1 | 0.001 | 0.001 | 0 | 131.25 | 105
CVW(I)(Z)>KRA(I)(Z)_110L1 | CVW_I_Z_110 | KRA_I_Z_110 | 1 | 0.012 | 0.026 | 0.004 | 123.75 | 99
DAL(I)(Z)>DAL(I)(T)_110L1 | DAL_I_Z_110 | DAL_I_T_110 | 1 | 0.019 | 0.042 | 0.004 | 131.25 | 105
DDK(I)(Z)>LOU(I)(Z)_110L1 | DDK_I_Z_110 | LOU_I_Z_110 | 1 | 0.026 | 0.058 | 0.005 | 123.75 | 99
DDK(I)(Z)>MLN(I)(Z)_110L1 | DDK_I_Z_110 | MLN_I_Z_110 | 1 | 0.012 | 0.026 | 0.002 | 123.75 | 99
DER(I)(Z)>KIN(I)(Z)_110L1 | DER_I_Z_110 | KIN_I_Z_110 | 1 | 0.012 | 0.05 | 0.005 | 123.75 | 99
DER(I)(Z)>TEN(I)(Z)_110L1 | DER_I_Z_110 | TEN_I_Z_110 | 1 | 0.014 | 0.073 | 0.009 | 92.5 | 74
TEN(I)(Z)>MAY(I)(Z)_110L1 | TEN_I_Z_110 | MAY_I_Z_110 | 1 | 0.014 | 0.073 | 0.009 | 92.5 | 74
DER(I)(Z)>TSB(I)(Z)_110L1 | DER_I_Z_110 | TSB_I_Z_110 | 1 | 0.031 | 0.068 | 0.006 | 123.75 | 99
DEY(I)(Z)>DAL(I)(T)_110L1 | DEY_I_Z_110 | DAL_I_T_110 | 1 | 0.004 | 0.021 | 0.002 | 222.5 | 178
DEY(I)(Z)>PLS(I)(Z)_110L1 | DEY_I_Z_110 | PLS_I_Z_110 | 1 | 0.031 | 0.157 | 0.017 | 222.5 | 178
DFR(I)(T)>DFR(I)(Z)_110L1 | DFR_I_T_110 | DFR_I_Z_110 | 1 | 1e-05 | 1e-05 | 1e-05 | 123.75 | 99
DFR(I)(Z)>MGT(I)(Z)_110L1 | DFR_I_Z_110 | MGT_I_Z_110 | 1 | 0.004 | 0.019 | 0.011 | 130 | 104
DGN(I)(Z)>WHE(I)(Z)_110L1 | DGN_I_Z_110 | WHE_I_Z_110 | 1 | 0.006 | 0.028 | 0.003 | 222.5 | 178
DGN(I)(Z)>RTO(I)(Z)_110L1 | DGN_I_Z_110 | RTO_I_Z_110 | 1 | 0.01 | 0.05 | 0.006 | 222.5 | 178
DMY(I)(Z)>CDN(I)(Z)_110L1 | DMY_I_Z_110 | CDN_I_Z_110 | 1 | 0.016 | 0.04 | 0.004 | 263.75 | 211
DMY(I)(Z)>MAC(I)(Z)_110L1 | DMY_I_Z_110 | MAC_I_Z_110 | 1 | 0.039 | 0.09 | 0.009 | 245 | 196
DON(N)(Z)>FIN(N)(Z)_110L1 | DON_N_Z_110 | FIN_N_Z_110 | 1 | 0.004 | 0.011 | 0.008 | 86.25 | 69
DON(N)(Z)>FIN(N)(Z)_110L2 | DON_N_Z_110 | FIN_N_Z_110 | 1 | 0.004 | 0.011 | 0.007 | 86.25 | 69
DON(N)(Z)>HAN(N)(Z)_110L1 | DON_N_Z_110 | HAN_N_Z_110 | 1 | 0.002 | 0.005 | 0.14 | 180 | 144
DON(N)(Z)>HAN(N)(Z)_110L2 | DON_N_Z_110 | HAN_N_Z_110 | 1 | 0.002 | 0.005 | 0.14 | 180 | 144
DRM(I)(Z)>CLO(I)(Z)_110L1 | DRM_I_Z_110 | CLO_I_Z_110 | 1 | 0.039 | 0.091 | 0.015 | 128.75 | 103
DRM(I)(Z)>LET(I)(Z)_110L1 | DRM_I_Z_110 | LET_I_Z_110 | 1 | 0.013 | 0.028 | 0.003 | 123.75 | 99
DRM(I)(Z)>MEE(I)(Z)_110L1 | DRM_I_Z_110 | MEE_I_Z_110 | 1 | 0.008 | 0.017 | 0.002 | 123.75 | 99
DRO(N)(Z)>ENN(N)(Z)_110L1 | DRO_N_Z_110 | ENN_N_Z_110 | 1 | 0.032 | 0.082 | 0.008 | 102.5 | 82
DRO(N)(Z)>ENN(N)(Z)_110L2 | DRO_N_Z_110 | ENN_N_Z_110 | 1 | 0.032 | 0.082 | 0.008 | 102.5 | 82
DRO(N)(Z)>OMA(N)(Z)_110L1 | DRO_N_Z_110 | OMA_N_Z_110 | 1 | 0.018 | 0.047 | 0.005 | 102.5 | 82
DRO(N)(Z)>OMA(N)(Z)_110L2 | DRO_N_Z_110 | OMA_N_Z_110 | 1 | 0.018 | 0.047 | 0.005 | 102.5 | 82
DRQ(N)(Z)>DRO(N)(Z)_110L1 | DRO_N_Z_110 | DRQ_N_Z_110 | 1 | 0.018 | 0.047 | 0.005 | 102.5 | 82
DRU(I)(Z)>ENN(I)(Z)_110L1 | DRU_I_Z_110 | ENN_I_Z_110 | 1 | 0.027 | 0.06 | 0.006 | 123.75 | 99
DRU(N)(Z)>TAN(N)(Z)_110L1 | DRU_N_Z_110 | TAN_N_Z_110 | 1 | 0.004 | 0.014 | 0.002 | 98.75 | 79
DRU(N)(Z)>TAN(N)(Z)_110L2 | DRU_N_Z_110 | TAN_N_Z_110 | 1 | 0.004 | 0.014 | 0.002 | 98.75 | 79
DRU(N)(Z)>TAN(N)(Z)_110L3 | DRU_N_Z_110 | TAN_N_Z_110 | 1 | 0.005 | 0.014 | 0.001 | 135 | 108
DRU(N)(Z)>TMN(N)(Z)_110L1 | DRU_N_Z_110 | TMN_N_Z_110 | 1 | 0.029 | 0.075 | 0.008 | 136.25 | 109
DRU(N)(Z)>TMN(N)(Z)_110L2 | DRU_N_Z_110 | TMN_N_Z_110 | 1 | 0.028 | 0.073 | 0.012 | 136.25 | 109
DRY(I)(Z)>GOR(I)(Z)_110L1 | DRY_I_Z_110 | GOR_I_Z_110 | 1 | 0.029 | 0.067 | 0.006 | 123.75 | 99
DRY(I)(Z)>LOU(I)(Z)_110L1 | DRY_I_Z_110 | LOU_I_Z_110 | 1 | 0.02 | 0.104 | 0.011 | 123.75 | 99
DRY(I)(Z)>PLA(I)(Z)_110L1 | DRY_I_Z_110 | PLA_I_Z_110 | 1 | 0.008 | 0.018 | 0.002 | 123.75 | 99
DRY(I)(Z)>OBE(I)(Z)_110L1 | DRY_I_Z_110 | OBE_I_Z_110 | 1 | 0.002 | 0.009 | 0.004 | 222.5 | 178
DSN(I)(Z)>KLS(I)(Z)_220L1 | DSN_I_Z_220 | KLS_I_Z_220 | 1 | 0.007 | 0.051 | 0.078 | 491.25 | 393
DSN(I)(Z)>MAY(I)(Z)_220L1 | DSN_I_Z_220 | MAY_I_Z_220 | 1 | 0.004 | 0.032 | 0.048 | 437.5 | 350
DSN(I)(Z)>MAY(I)(Z)_220L2 | DSN_I_Z_220 | MAY_I_Z_220 | 1 | 0.004 | 0.026 | 0.04 | 437.5 | 350
DSN(I)(Z)>MAY(I)(Z)_220L3 | DSN_I_Z_220 | MAY_I_Z_220 | 1 | 0.004 | 0.027 | 0.040 | 542.5 | 434
DSN(I)(Z)>MP(I)(Z)_380L1 | DSN_I_Z_380 | MP_I_Z_380 | 1 | 0.004 | 0.044 | 1.14 | 1603.75 | 1283
DSN(I)(Z)>TH(I)(Z)_220L1 | DSN_I_Z_220 | TH_I_Z_220 | 1 | 0.003 | 0.022 | 0.144 | 438.75 | 351
DTN(I)(Z)>BLC(I)(Z)_110L1 | DTN_I_Z_110 | BLC_I_Z_110 | 1 | 0.004 | 0.009 | 0.049 | 175 | 140
DTN(I)(Z)>FIN(I)(Z)_110L1 | DTN_I_Z_110 | FIN_I_Z_110 | 1 | 0.002 | 0.014 | 0.111 | 175 | 140
DTN(I)(Z)>KLM(I)(Z)_110L1 | DTN_I_Z_110 | KLM_I_Z_110 | 1 | 0.002 | 0.005 | 0.032 | 175 | 140
DUN(N)(Z)>OMA(N)(Z)_110L1 | DUN_N_Z_110 | OMA_N_Z_110 | 1 | 0.042 | 0.124 | 0.012 | 232.5 | 186
DUN(N)(Z)>TMN(N)(Z)_110L1 | DUN_N_Z_110 | TMN_N_Z_110 | 1 | 0.004 | 0.017 | 0.005 | 196.25 | 157
DUN(N)(Z)>TMN(N)(Z)_110L2 | DUN_N_Z_110 | TMN_N_Z_110 | 1 | 0.009 | 0.023 | 0.002 | 180 | 144
DUN(N)(Z)>TMN(N)(Z)_110L3 | DUN_N_Z_110 | TMN_N_Z_110 | 1 | 0.004 | 0.02 | 0.019 | 232.5 | 186
ENN(I)(Z)>SLC(I)(Z)_110L1 | ENN_I_Z_110 | SLC_I_Z_110 | 1 | 0.003 | 0.048 | 0.271 | 243.75 | 195
FAS(I)(Z)>FAS(I)(Z)_110L1 | FAS_I_Z_110 | FAS_I_Z_110 | 0 | 0.008 | 0.017 | 0.002 | 131.25 | 105
FIN(I)(Z)>GLA(I)(Z)_110L1 | FIN_I_Z_110 | GLA_I_Z_110 | 1 | 0.022 | 0.048 | 0.005 | 131.25 | 105
FIN(I)(Z)>GRA(I)(Z)_110L1 | FIN_I_Z_110 | GRA_I_Z_110 | 1 | 0.005 | 0.012 | 0.236 | 148.75 | 119
FIN(I)(Z)>HN(I)(Z)_220L1 | FIN_I_Z_220 | HN_I_Z_220 | 1 | 0 | 0.001 | 0.038 | 741.25 | 593
FIN(I)(Z)>MCD(I)(Z)_110L1 | FIN_I_Z_110 | MCD_I_Z_110 | 1 | 0.003 | 0.007 | 0.141 | 148.75 | 119
FIN(I)(Z)>NW(I)(Z)_220L1 | FIN_I_Z_220 | NW_I_Z_220 | 1 | 0.001 | 0.004 | 0.67 | 415 | 332
FIN(I)(Z)>POP(I)(Z)_110L1 | FIN_I_Z_110 | POP_I_Z_110 | 1 | 0.002 | 0.005 | 0.026 | 150 | 120
FIN(I)(Z)>PTN(I)(Z)_110L1 | FIN_I_Z_110 | PTN_I_Z_110 | 1 | 0.003 | 0.01 | 0.006 | 100 | 80
FIN(I)(Z)>SHL(I)(Z)_220L1 | FIN_I_Z_220 | SHL_I_Z_220 | 1 | 0 | 0.005 | 0.367 | 670 | 536
FIN(I)(Z)>SVN(I)(Z)_110L1 | FIN_I_Z_110 | SVN_I_Z_110 | 1 | 0.039 | 0.104 | 0.056 | 131.25 | 105
FIN(N)(Z)>HAN(N)(Z)_110L1 | FIN_N_Z_110 | HAN_N_Z_110 | 1 | 0.001 | 0.003 | 0.022 | 180 | 144
FIN(N)(Z)>HAN(N)(Z)_110L2 | FIN_N_Z_110 | HAN_N_Z_110 | 1 | 0.001 | 0.003 | 0.022 | 180 | 144
FLA(I)(Z)>GIL(I)(Z)_110L1 | FLA_I_Z_110 | GIL_I_Z_110 | 1 | 0.017 | 0.037 | 0.003 | 131.25 | 105
FLA(I)(Z)>LOU(I)(Z)_220L1 | FLA_I_Z_220 | LOU_I_Z_220 | 1 | 0.013 | 0.098 | 0.145 | 480 | 384
FLA(I)(Z)>SLB(I)(Z)_110L1 | FLA_I_Z_110 | SLB_I_Z_110 | 1 | 0.034 | 0.075 | 0.007 | 123.75 | 99
FLA(I)(Z)>SLI(I)(Z)_110L1 | FLA_I_Z_110 | SLI_I_Z_110 | 1 | 0.079 | 0.174 | 0.016 | 123.75 | 99
FLA(I)(Z)>SRA(I)(Z)_220L1 | FLA_I_Z_220 | SRA_I_Z_220 | 1 | 0.006 | 0.047 | 0.077 | 542.5 | 434
FLA(I)(Z)>TON(I)(Z)_110L1 | FLA_I_Z_110 | TON_I_Z_110 | 1 | 0.05 | 0.111 | 0.01 | 122.5 | 98
FRS(I)(Z)>HAR(I)(Z)_110L1 | FRS_I_Z_110 | HAR_I_Z_110 | 1 | 0.002 | 0.004 | 0.03 | 133.75 | 107
FRS(I)(Z)>HEU(I)(Z)_110L1 | FRS_I_Z_110 | HEU_I_Z_110 | 1 | 0.002 | 0.004 | 0.024 | 175 | 140
FRS(I)(Z)>INC(I)(Z)_110L1 | FRS_I_Z_110 | INC_I_Z_110 | 1 | 0.004 | 0.01 | 0.073 | 133.75 | 107
FRS(I)(Z)>TRN(I)(Z)_110L1 | FRS_I_Z_110 | TRN_I_Z_110 | 1 | 0.002 | 0.004 | 0.028 | 175 | 140
GAL(I)(Z)>SAL(I)(Z)_110L1 | GAL_I_Z_110 | SAL_I_Z_110 | 1 | 0.003 | 0.003 | 0.067 | 123.75 | 99
GAL(I)(Z)>SEE(I)(Z)_110L1 | GAL_I_Z_110 | SEE_I_Z_110 | 1 | 0.005 | 0.031 | 0.138 | 123.75 | 99
CDU(I)(Z)>GAN(I)(Z)_110L1 | GAN_I_Z_110 | CDU_I_Z_110 | 1 | 0.007 | 0.036 | 0.004 | 222.5 | 178
GCA(I)(Z)>GRI(I)(T)_110L1 | GCA_I_Z_110 | GRI_I_T_110 | 1 | 0.009 | 0.029 | 0.006 | 128.75 | 103
GCA(I)(Z)>INC(I)(Z)_110L1 | GCA_I_Z_110 | INC_I_Z_110 | 1 | 0.008 | 0.025 | 0.009 | 128.75 | 103
GCA(I)(Z)>INC(I)(Z)_110L2 | GCA_I_Z_110 | INC_I_Z_110 | 1 | 0.008 | 0.025 | 0.009 | 128.75 | 103
GCA(I)(Z)>NAN(I)(Z)_110L1 | GCA_I_Z_110 | NAN_I_Z_110 | 1 | 0.001 | 0.002 | 0.011 | 150 | 120
GCA(I)(Z)>NAN(I)(Z)_110L2 | GCA_I_Z_110 | NAN_I_Z_110 | 1 | 0.001 | 0.002 | 0.011 | 150 | 120
GGO(I)(Z)>RAF(I)(Z)_220L1 | GGO_I_Z_220 | RAF_I_Z_220 | 1 | 0 | 0.005 | 0.414 | 712.5 | 570
GI(I)(Z)>KKY(I)(Z)_110L1 | GI_I_Z_110 | KKY_I_Z_110 | 1 | 0.031 | 0.16 | 0.017 | 123.75 | 99
GI(I)(Z)>KLS(I)(Z)_220L1 | GI_I_Z_220 | KLS_I_Z_220 | 1 | 0.008 | 0.061 | 0.101 | 491.25 | 393
GI(I)(Z)>LWD(I)(Z)_220L1 | GI_I_Z_220 | LWD_I_Z_220 | 1 | 0.006 | 0.042 | 0.07 | 542.5 | 434
GI(I)(Z)>LWN(I)(Z)_220L1 | GI_I_Z_220 | LWN_I_Z_220 | 1 | 1e-05 | 1e-05 | 0.011 | 741.25 | 593
GI(I)(Z)>WAT(I)(Z)_110L1 | GI_I_Z_110 | WAT_I_Z_110 | 1 | 0.007 | 0.038 | 0.004 | 222.5 | 178
GI(I)(Z)>WAT(I)(Z)_110L2 | GI_I_Z_110 | WAT_I_Z_110 | 1 | 0.008 | 0.042 | 0.005 | 222.5 | 178
GI(I)(Z)>ROP(I)(Z)_110L1 | GI_I_Z_110 | ROP_I_Z_110 | 1 | 0.011 | 0.056 | 0.006 | 222.5 | 178
ROP(I)(Z)>WEX(I)(Z)_110L1 | ROP_I_Z_110 | WEX_I_Z_110 | 1 | 0.011 | 0.056 | 0.006 | 222.5 | 178
GLA(I)(Z)>SVN(I)(Z)_110L1 | GLA_I_Z_110 | SVN_I_Z_110 | 1 | 0.017 | 0.055 | 0.052 | 170 | 136
GLE(I)(Z)>KCR(I)(Z)_110L1 | GLE_I_Z_110 | KCR_I_Z_110 | 1 | 0.003 | 0.013 | 0.124 | 152.5 | 122
GLE(N)(Z)>KEL(N)(Z)_110L1 | GLE_N_Z_110 | KEL_N_Z_110 | 1 | 0.027 | 0.068 | 0.027 | 102.5 | 82
GLE(N)(Z)>KEL(N)(Z)_110L2 | GLE_N_Z_110 | KEL_N_Z_110 | 1 | 0.027 | 0.068 | 0.027 | 102.5 | 82
GOL(I)(Z)>GOL(I)(T)_110L1 | GOL_I_Z_110 | GOL_I_T_110 | 1 | 0.006 | 0.014 | 0.001 | 131.25 | 105
GOR(I)(Z)>LOU(I)(Z)_220L1 | GOR_I_Z_220 | LOU_I_Z_220 | 1 | 0.004 | 0.028 | 0.042 | 542.5 | 434
GOR(I)(Z)>MAY(I)(Z)_220L1 | GOR_I_Z_220 | MAY_I_Z_220 | 1 | 0.005 | 0.037 | 0.055 | 437.5 | 350
GOR(I)(Z)>MTH(I)(Z)_110L1 | GOR_I_Z_110 | MTH_I_Z_110 | 1 | 0.026 | 0.087 | 0.012 | 123.75 | 99
GOR(I)(Z)>NAV(I)(Z)_110L1 | GOR_I_Z_110 | NAV_I_Z_110 | 1 | 0.008 | 0.019 | 0.002 | 123.75 | 99
GOR(I)(Z)>NAV(I)(Z)_110L2 | GOR_I_Z_110 | NAV_I_Z_110 | 1 | 0.009 | 0.022 | 0.002 | 123.75 | 99
GOR(I)(Z)>NAV(I)(Z)_110L3 | GOR_I_Z_110 | NAV_I_Z_110 | 1 | 0.005 | 0.017 | 0.007 | 123.75 | 99
GOR(I)(Z)>GRH(I)(Z)_110L1 | GOR_I_Z_110 | GRH_I_Z_110 | 1 | 0.03 | 0.034 | 0.003 | 123.75 | 99
GRH(I)(Z)>PLA(I)(Z)_110L1 | GRH_I_Z_110 | PLA_I_Z_110 | 1 | 0.03 | 0.034 | 0.003 | 123.75 | 99
GOR(N)(Z)>OMA(N)(Z)_110L1 | GOR_N_Z_110 | OMA_N_Z_110 | 1 | 0.009 | 0.067 | 0.02 | 250 | 200
GOR(N)(Z)>TMN(N)(Z)_110L1 | GOR_N_Z_110 | TMN_N_Z_110 | 1 | 0.019 | 0.161 | 0.029 | 250 | 200
GRA(I)(Z)>NBY(I)(Z)_110L1 | GRA_I_Z_110 | NBY_I_Z_110 | 1 | 0.002 | 0.005 | 0.089 | 148.75 | 119
GRI(I)(T)>MAY(I)(Z)_110L1 | GRI_I_T_110 | MAY_I_Z_110 | 1 | 0.003 | 0.009 | 0.001 | 131.25 | 105
GRI(I)(Z)>GRI(I)(T)_110L1 | GRI_I_Z_110 | GRI_I_T_110 | 1 | 0.002 | 0.004 | 0 | 131.25 | 105
GRO(I)(Z)>BVK(I)(Z)_110L1 | GRO_I_Z_110 | BVK_I_Z_110 | 1 | 0.002 | 0.002 | 0.054 | 243.75 | 195
HAN(N)(Z)>BYC(N)(Z)_275L1 | HAN_N_Z_275 | BYC_N_Z_275 | 1 | 0.002 | 0.019 | 0.112 | 887.5 | 710
HAN(N)(Z)>LIS(N)(Z)_110L1 | HAN_N_Z_110 | LIS_N_Z_110 | 1 | 0.01 | 0.026 | 0.018 | 102.5 | 82
HAN(N)(Z)>LIS(N)(Z)_110L2 | HAN_N_Z_110 | LIS_N_Z_110 | 1 | 0.009 | 0.026 | 0.018 | 100 | 80
HAR(I)(Z)>RE(I)(Z)_110L1 | HAR_I_Z_110 | RE_I_Z_110 | 1 | 0.005 | 0.01 | 0.073 | 133.75 | 107
HEU(I)(Z)>INC(I)(Z)_110L1 | HEU_I_Z_110 | INC_I_Z_110 | 1 | 0.003 | 0.005 | 0.036 | 175 | 140
HWN(I)(Z)>MGT(I)(Z)_110L1 | HWN_I_Z_110 | MGT_I_Z_110 | 1 | 0.013 | 0.059 | 0.006 | 170 | 136
HWN(I)(Z)>KIN(I)(Z)_110L1 | HWN_I_Z_110 | KIN_I_Z_110 | 1 | 0.006 | 0.019 | 0.003 | 170 | 136
HWN(I)(Z)>DFR(I)(T)_110L1 | HWN_I_Z_110 | DFR_I_T_110 | 1 | 0.016 | 0.08 | 0.009 | 130 | 104
IA(I)(Z)>MAC(I)(Z)_110L1 | IA_I_Z_110 | MAC_I_Z_110 | 1 | 0.027 | 0.062 | 0.006 | 245 | 196
IKE(I)(Z)>IKE(I)(T)_110L1 | IKE_I_Z_110 | IKE_I_T_110 | 1 | 0 | 0.001 | 0 | 100 | 80
INC(I)(Z)>ISH(I)(Z)_220L1 | INC_I_Z_220 | ISH_I_Z_220 | 1 | 0 | 0.005 | 0.33 | 702.5 | 562
INC(I)(Z)>MIL(I)(Z)_110L1 | INC_I_Z_110 | MIL_I_Z_110 | 1 | 0.004 | 0.009 | 0.051 | 150 | 120
INC(I)(Z)>PB(I)(Z)_220L1 | INC_I_Z_220 | PB_I_Z_220 | 1 | 0.001 | 0.004 | 0.498 | 333.75 | 267
INC(I)(Z)>PB(I)(Z)_220L2 | INC_I_Z_220 | PB_I_Z_220 | 1 | 0 | 0.003 | 0.722 | 438.75 | 351
ISH(I)(Z)>SHL(I)(Z)_220L1 | ISH_I_Z_220 | SHL_I_Z_220 | 1 | 0 | 0.001 | 0.036 | 741.25 | 593
KBY(I)(Z)>KRA(I)(Z)_110L1 | KBY_I_Z_110 | KRA_I_Z_110 | 1 | 0.008 | 0.039 | 0.004 | 222.5 | 178
KBY(I)(Z)>KRA(I)(Z)_110L2 | KBY_I_Z_110 | KRA_I_Z_110 | 1 | 0.018 | 0.043 | 0.004 | 123.75 | 99
KBY(I)(Z)>MAL(I)(Z)_110L1 | KBY_I_Z_110 | MAL_I_Z_110 | 1 | 0.018 | 0.095 | 0.01 | 167.5 | 134
KBY(I)(Z)>MR(I)(Z)_110L1 | KBY_I_Z_110 | MR_I_Z_110 | 1 | 0.004 | 0.015 | 0.004 | 128.75 | 103
KBY(I)(Z)>MR(I)(Z)_110L2 | KBY_I_Z_110 | MR_I_Z_110 | 1 | 0.005 | 0.015 | 0.004 | 128.75 | 103
KEL(N)(Z)>KPS(N)(Z)_275L1 | KEL_N_Z_275 | KPS_N_Z_275 | 1 | 0.001 | 0.012 | 0.075 | 887.5 | 710
KEL(N)(Z)>KPS(N)(Z)_275L2 | KEL_N_Z_275 | KPS_N_Z_275 | 1 | 0.001 | 0.012 | 0.075 | 887.5 | 710
KEL(N)(Z)>MAG(N)(Z)_275L1 | KEL_N_Z_275 | MAG_N_Z_275 | 1 | 0.001 | 0.013 | 0.08 | 887.5 | 710
KEL(N)(Z)>RSK(N)(Z)_110L1 | KEL_N_Z_110 | RSK_N_Z_110 | 1 | 0.039 | 0.133 | 0.013 | 231.25 | 185
KER(I)(Z)>OUG(I)(T)_110L1 | KER_I_Z_110 | OUG_I_T_110 | 1 | 0.014 | 0.074 | 0.008 | 222.5 | 178
KIN(I)(Z)>DFR(I)(T)_110L1 | KIN_I_Z_110 | DFR_I_T_110 | 1 | 0.021 | 0.096 | 0.01 | 123.75 | 99
KIN(I)(Z)>MUL(I)(Z)_110L1 | KIN_I_Z_110 | MUL_I_Z_110 | 1 | 0.016 | 0.077 | 0.023 | 222.5 | 178
KLH(I)(Z)>THU(I)(Z)_110L1 | KLH_I_Z_110 | THU_I_Z_110 | 1 | 0.013 | 0.069 | 0.008 | 222.5 | 178
KLM(I)(Z)>NBY(I)(Z)_110L1 | KLM_I_Z_110 | NBY_I_Z_110 | 1 | 0.001 | 0.001 | 0.02 | 148.75 | 119
KLM(I)(Z)>POP(I)(Z)_110L1 | KLM_I_Z_110 | POP_I_Z_110 | 1 | 0.003 | 0.007 | 0.036 | 150 | 120
KLN(I)(Z)>CUR(I)(Z)_110L1 | KLN_I_Z_110 | CUR_I_Z_110 | 1 | 0.011 | 0.048 | 0.005 | 170 | 136
KLN(I)(Z)>KPG(I)(Z)_220L1 | KLN_I_Z_220 | KPG_I_Z_220 | 1 | 0.008 | 0.061 | 0.114 | 542.5 | 434
KLN(I)(Z)>KRA(I)(Z)_220L1 | KLN_I_Z_220 | KRA_I_Z_220 | 1 | 0.013 | 0.069 | 0.107 | 640 | 512
KLN(I)(Z)>LIM(I)(Z)_110L1 | KLN_I_Z_110 | LIM_I_Z_110 | 1 | 0.014 | 0.031 | 0.003 | 123.75 | 99
KLN(I)(Z)>LIM(I)(Z)_110L2 | KLN_I_Z_110 | LIM_I_Z_110 | 1 | 0.018 | 0.04 | 0.009 | 100 | 80
KLN(I)(Z)>SH(I)(Z)_220L1 | KLN_I_Z_220 | SH_I_Z_220 | 1 | 0.014 | 0.08 | 0.12 | 336.25 | 269
KLN(I)(Z)>SNG(I)(Z)_110L1 | KLN_I_Z_110 | SNG_I_Z_110 | 1 | 0.003 | 0.013 | 0.003 | 222.5 | 178
KLP(I)(Z)>CNG(I)(Z)_110L1 | KLP_I_Z_110 | CNG_I_Z_110 | 1 | 0 | 0.001 | 0.003 | 175 | 140
KLP(I)(Z)>KNR(I)(Z)_110L1 | KLP_I_Z_110 | KNR_I_Z_110 | 1 | 0.015 | 0.05 | 0.005 | 170 | 136
KLP(I)(Z)>KNR(I)(Z)_220L1 | KLP_I_Z_220 | KNR_I_Z_220 | 1 | 0.003 | 0.015 | 0.054 | 913.75 | 731
KLP(I)(Z)>KNR(I)(Z)_220L2 | KLP_I_Z_220 | KNR_I_Z_220 | 1 | 0 | 0.01 | 0.971 | 913.75 | 731
KLP(I)(Z)>MP(I)(Z)_220L1 | KLP_I_Z_220 | MP_I_Z_220 | 1 | 0 | 0.002 | 0.236 | 825 | 660
KLP(I)(Z)>MP(I)(Z)_220L2 | KLP_I_Z_220 | MP_I_Z_220 | 1 | 0 | 0.002 | 0.236 | 825 | 660
KLP(I)(Z)>RAT(I)(Z)_110L1 | KLP_I_Z_110 | RAT_I_Z_110 | 1 | 0.033 | 0.107 | 0.018 | 170 | 136
KLP(I)(Z)>TB(I)(Z)_110L1 | KLP_I_Z_110 | TB_I_Z_110 | 1 | 0.002 | 0.006 | 0.001 | 123.75 | 99
KLP(I)(Z)>TB(I)(Z)_110L2 | KLP_I_Z_110 | TB_I_Z_110 | 1 | 0.002 | 0.006 | 0.001 | 123.75 | 99
KLP(I)(Z)>TB(I)(Z)_220L1 | KLP_I_Z_220 | TB_I_Z_220 | 1 | 0 | 0.002 | 0.026 | 437.5 | 350
KLP(I)(Z)>TB(I)(Z)_220L2 | KLP_I_Z_220 | TB_I_Z_220 | 1 | 0 | 0.002 | 0.028 | 437.5 | 350
KLP(I)(Z)>TRL(I)(Z)_110L1 | KLP_I_Z_110 | TRL_I_Z_110 | 1 | 0.06 | 0.135 | 0.013 | 123.75 | 99
KLP(I)(Z)>TRL(I)(Z)_110L2 | KLP_I_Z_110 | TRL_I_Z_110 | 1 | 0.027 | 0.14 | 0.023 | 222.5 | 178
KLS(I)(Z)>KKY(I)(Z)_110L1 | KLS_I_Z_110 | KKY_I_Z_110 | 1 | 0.053 | 0.118 | 0.011 | 123.75 | 99
KMT(N)(Z)>SLK(N)(Z)_110L1 | KMT_N_Z_110 | SLK_N_Z_110 | 1 | 0.007 | 0.018 | 0.006 | 136.25 | 109
KMT(N)(Z)>STR(N)(Z)_110L1 | KMT_N_Z_110 | STR_N_Z_110 | 1 | 0.008 | 0.037 | 0.004 | 178.75 | 143
KNR(I)(Z)>BYH(I)(Z)_220L1 | KNR_I_Z_220 | BYH_I_Z_220 | 1 | 0.005 | 0.033 | 0.061 | 542.5 | 434
KNR(I)(Z)>TRI(I)(Z)_110L1 | KNR_I_Z_110 | TRI_I_Z_110 | 1 | 0.003 | 0.013 | 0.005 | 222.5 | 178
KNR(I)(Z)>TRI(I)(Z)_110L2 | KNR_I_Z_110 | TRI_I_Z_110 | 1 | 0.004 | 0.013 | 0.004 | 123.75 | 99
KNY(I)(Z)>BUF(I)(Z)_110L1 | KNY_I_Z_110 | BUF_I_Z_110 | 1 | 0 | 0.001 | 0.006 | 175 | 140
KNY(I)(Z)>KLH(I)(Z)_110L1 | KNY_I_Z_110 | KLH_I_Z_110 | 1 | 0.003 | 0.015 | 0.107 | 237.5 | 190
KNY(I)(Z)>SAL(I)(Z)_110L1 | KNY_I_Z_110 | SAL_I_Z_110 | 1 | 0.019 | 0.063 | 0.081 | 243.75 | 195
KNY(I)(Z)>SCR(I)(Z)_110L1 | KNY_I_Z_110 | SCR_I_Z_110 | 1 | 0.031 | 0.108 | 0.04 | 168.75 | 135
KNY(I)(Z)>UGL(I)(Z)_110L1 | KNY_I_Z_110 | UGL_I_Z_110 | 1 | 0.001 | 0.004 | 0.04 | 243.75 | 195
KPS(N)(Z)>TAN(N)(Z)_275L1 | KPS_N_Z_275 | TAN_N_Z_275 | 1 | 0.004 | 0.034 | 0.206 | 887.5 | 710
KRA(I)(Z)>BAR(I)(T)_110L1 | KRA_I_Z_110 | BAR_I_T_110 | 1 | 0.02 | 0.065 | 0.007 | 170 | 136
KRA(I)(Z)>LGT(I)(T)_110L1 | KRA_I_Z_110 | LGT_I_Z_110 | 1 | 0.012 | 0.027 | 0.004 | 131.25 | 105
KRA(I)(Z)>MEN(I)(Z)_110L1 | KRA_I_Z_110 | MEN_I_Z_110 | 1 | 0.002 | 0.002 | 0.034 | 155 | 124
KRA(I)(Z)>MID(I)(Z)_110L1 | KRA_I_Z_110 | MID_I_Z_110 | 1 | 0.017 | 0.037 | 0.004 | 123.75 | 99
KRA(I)(Z)>RAF(I)(Z)_220L1 | KRA_I_Z_220 | RAF_I_Z_220 | 1 | 0.002 | 0.017 | 0.026 | 441.25 | 353
KRA(I)(Z)>WHO(I)(Z)_110L1 | KRA_I_Z_110 | WHO_I_Z_110 | 1 | 0.026 | 0.135 | 0.015 | 222.5 | 178
KTL(I)(Z)>MAY(I)(Z)_110L1 | KTL_I_Z_110 | MAY_I_Z_110 | 1 | 0.022 | 0.072 | 0.007 | 123.75 | 99
KTL(I)(Z)>MON(I)(Z)_110L1 | KTL_I_Z_110 | MON_I_Z_110 | 1 | 0.009 | 0.03 | 0.003 | 170 | 136
KTN(I)(Z)>WAT(I)(Z)_110L1 | KTN_I_Z_110 | WAT_I_Z_110 | 1 | 0.001 | 0.003 | 0.039 | 123.75 | 99
KUD(I)(Z)>CBT(I)(Z)_110L1 | KUD_I_Z_110 | CBT_I_Z_110 | 1 | 0 | 0.001 | 0.008 | 233.75 | 187
KUR(I)(Z)>NAV(I)(Z)_110L1 | KUR_I_Z_110 | NAV_I_Z_110 | 1 | 0.01 | 0.021 | 0.002 | 123.75 | 99
KYT(I)(Z)>MAY(I)(Z)_220L1 | KYT_I_Z_220 | MAY_I_Z_220 | 1 | 0.003 | 0.011 | 0.112 | 951.25 | 761
KYT(I)(Z)>WOO(I)(Z)_220L1 | KYT_I_Z_220 | WOO_I_Z_220 | 1 | 0.003 | 0.011 | 0.112 | 951.25 | 761
LA(I)(Z)>MUL(I)(Z)_110L1 | LA_I_Z_110 | MUL_I_Z_110 | 1 | 0.01 | 0.16 | 0.015 | 123.75 | 99
LA(I)(Z)>RIC(I)(Z)_110L1 | LA_I_Z_110 | RIC_I_Z_110 | 1 | 0.024 | 0.054 | 0.007 | 123.75 | 99
LA(I)(Z)>RIC(I)(Z)_110L2 | LA_I_Z_110 | RIC_I_Z_110 | 1 | 0.02 | 0.043 | 0.005 | 123.75 | 99
LA(I)(Z)>SLB(I)(Z)_110L1 | LA_I_Z_110 | SLB_I_Z_110 | 1 | 0.014 | 0.031 | 0.003 | 123.75 | 99
LNA(I)(Z)>TIV(I)(Z)_110L1 | LNA_I_Z_110 | TIV_I_Z_110 | 1 | 0.035 | 0.111 | 0.011 | 170 | 136
LCK(I)(Z)>MUL(I)(Z)_110L1 | LCK_I_Z_110 | MUL_I_Z_110 | 1 | 0.019 | 0.039 | 0.261 | 155 | 124
LET(I)(Z)>GOL(I)(T)_110L1 | LET_I_Z_110 | GOL_I_T_110 | 1 | 0.058 | 0.132 | 0.014 | 123.75 | 99
LET(I)(Z)>STR(N)(Z)_110L1 | LET_I_Z_110 | STR_N_Z_110 | 1 | 0.035 | 0.076 | 0.007 | 123.75 | 99
LET(I)(Z)>TIV(I)(Z)_110L1 | LET_I_Z_110 | TIV_I_Z_110 | 1 | 0.047 | 0.151 | 0.015 | 170 | 136
LET(I)(Z)>TLK(I)(Z)_110L1 | LET_I_Z_110 | TLK_I_Z_110 | 1 | 0.051 | 0.117 | 0.012 | 131.25 | 105
LET(I)(Z)>LNA(I)(Z)_110L1 | LET_I_Z_110 | LNA_I_Z_110 | 1 | 0.013 | 0.041 | 0.004 | 170 | 136
LIB(I)(Z)>MR(I)(Z)_110L1 | LIB_I_Z_110 | MR_I_Z_110 | 1 | 0.001 | 0.003 | 0.017 | 125 | 100
LIB(I)(Z)>MR(I)(Z)_110L2 | LIB_I_Z_110 | MR_I_Z_110 | 1 | 0.002 | 0.003 | 0.017 | 123.75 | 99
LIM(I)(Z)>MTN(I)(Z)_110L1 | LIM_I_Z_110 | MTN_I_Z_110 | 1 | 0.005 | 0.025 | 0.003 | 222.5 | 178
LIM(I)(Z)>RAT(I)(Z)_110L1 | LIM_I_Z_110 | RAT_I_Z_110 | 1 | 0.041 | 0.096 | 0.012 | 123.75 | 99
LIS(I)(Z)>LOU(I)(Z)_110L1 | LIS_I_Z_110 | LOU_I_Z_110 | 1 | 0.063 | 0.139 | 0.013 | 123.75 | 99
LIS(I)(Z)>LSA(I)(T)_110L1 | LIS_I_Z_110 | LSA_I_T_110 | 1 | 0.0305 | 0.0675 | 0.0065 | 123.75 | 99
LSA(I)(T)>SKL(I)(Z)_110L1 | LSA_I_T_110 | SKL_I_Z_110 | 1 | 0.0305 | 0.0675 | 0.0065 | 123.75 | 99
LIS(N)(Z)>TAN(N)(Z)_110L1 | LIS_N_Z_110 | TAN_N_Z_110 | 1 | 0.04 | 0.106 | 0.01 | 102.5 | 82
LIS(N)(Z)>TAN(N)(Z)_110L2 | LIS_N_Z_110 | TAN_N_Z_110 | 1 | 0.034 | 0.1 | 0.009 | 100 | 80
LOU(I)(Z)>MLN(I)(Z)_110L1 | LOU_I_Z_110 | MLN_I_Z_110 | 1 | 0.02 | 0.045 | 0.004 | 123.75 | 99
LOU(I)(Z)>MTH(I)(Z)_110L1 | LOU_I_Z_110 | MTH_I_Z_110 | 1 | 0.024 | 0.052 | 0.005 | 123.75 | 99
LOU(I)(Z)>RRU(I)(Z)_110L1 | LOU_I_Z_110 | RRU_I_Z_110 | 1 | 0.058 | 0.133 | 0.014 | 118.75 | 95
LOU(I)(Z)>TAN(N)(Z)_275L1 | LOU_I_Z_275 | TAN_N_Z_275 | 1 | 0.003 | 0.021 | 0.127 | 887.5 | 710
LOU(I)(Z)>TAN(N)(Z)_275L2 | LOU_I_Z_275 | TAN_N_Z_275 | 1 | 0.003 | 0.021 | 0.127 | 887.5 | 710
LOU(I)(Z)>WOO(I)(Z)_220L1 | LOU_I_Z_220 | WOO_I_Z_220 | 1 | 0.007 | 0.053 | 0.08 | 437.5 | 350
LSA(I)(Z)>LSA(I)(T)_110L1 | LSA_I_Z_110 | LSA_I_T_110 | 1 | 0.0001 | 0.0001 | 0.006 | 150 | 120
LSN(I)(Z)>THU(I)(Z)_110L1 | LSN_I_Z_110 | THU_I_Z_110 | 1 | 0.016 | 0.036 | 0.003 | 130 | 104
MAG(N)(Z)>TMN(N)(Z)_275L1 | MAG_N_Z_275 | TMN_N_Z_275 | 1 | 0.001 | 0.011 | 0.065 | 887.5 | 710
MAG(N)(Z)>TMN(N)(Z)_275L2 | MAG_N_Z_275 | TMN_N_Z_275 | 1 | 0.001 | 0.011 | 0.065 | 887.5 | 710
MAY(I)(Z)>BLK(I)(Z)_110L1 | MAY_I_Z_110 | BLK_I_Z_110 | 1 | 0.032 | 0.103 | 0.011 | 123.75 | 99
MAY(I)(Z)>GRI(I)(Z)_110L1 | MAY_I_Z_110 | GRI_I_Z_110 | 1 | 0.002 | 0.007 | 0.002 | 123.75 | 99
MAY(I)(Z)>RNW(I)(Z)_110L1 | MAY_I_Z_110 | RNW_I_Z_110 | 1 | 0.008 | 0.024 | 0.002 | 100 | 80
MAY(I)(Z)>RYB(I)(Z)_110L1 | MAY_I_Z_110 | RYB_I_Z_110 | 1 | 0.009 | 0.03 | 0.005 | 222.5 | 178
MAY(I)(Z)>SH(I)(Z)_220L1 | MAY_I_Z_220 | SH_I_Z_220 | 1 | 0.017 | 0.094 | 0.142 | 336.25 | 269
MAY(I)(Z)>TH(I)(Z)_220L1 | MAY_I_Z_220 | TH_I_Z_220 | 1 | 0.006 | 0.044 | 0.184 | 406.25 | 325
MAY(I)(Z)>WOO(I)(Z)_220L1 | MAY_I_Z_220 | WOO_I_Z_220 | 1 | 0.003 | 0.02 | 0.03 | 437.5 | 350
MCD(I)(Z)>NQS(I)(Z)_110L1 | MCD_I_Z_110 | NQS_I_Z_110 | 1 | 0.001 | 0.002 | 0.036 | 148.75 | 119
MCD(I)(Z)>WOL(I)(Z)_110L1 | MCD_I_Z_110 | WOL_I_Z_110 | 1 | 0.001 | 0.002 | 0.009 | 150 | 120
MHL(I)(Z)>RE(I)(Z)_110L1 | MHL_I_Z_110 | RE_I_Z_110 | 1 | 0.002 | 0.004 | 0.03 | 175 | 140
MHL(I)(Z)>TRN(I)(Z)_110L1 | MHL_I_Z_110 | TRN_I_Z_110 | 1 | 0.001 | 0.002 | 0.014 | 175 | 140
MID(I)(Z)>WHI(I)(Z)_110L1 | MID_I_Z_110 | WHI_I_Z_110 | 1 | 0.03 | 0.069 | 0.007 | 123.75 | 99
MID(I)(Z)>LGT(I)(Z)_110L1 | MID_I_Z_110 | LGT_I_Z_110 | 1 | 0.005 | 0.011 | 0.003 | 131.25 | 105
MIL(I)(Z)>RE(I)(Z)_110L1 | MIL_I_Z_110 | RE_I_Z_110 | 1 | 0.003 | 0.005 | 0.075 | 125 | 100
MIL(I)(Z)>RE(I)(Z)_110L2 | MIL_I_Z_110 | RE_I_Z_110 | 1 | 0.003 | 0.006 | 0.034 | 150 | 120
MKL(N)(Z)>OMA(N)(Z)_110L1 | MKL_N_Z_110 | OMA_N_Z_110 | 1 | 0.028 | 0.113 | 0.015 | 173.75 | 139
MLC(I)(Z)>TSB(I)(Z)_110L1 | MLC_I_Z_110 | TSB_I_Z_110 | 1 | 0.016 | 0.056 | 0.028 | 168.75 | 135
MNH(I)(Z)>MTA(I)(Z)_110L1 | MNH_I_Z_110 | MTA_I_Z_110 | 1 | 0.001 | 0.003 | 0.033 | 237.5 | 190
MOY(I)(Z)>TAW(I)(Z)_110L1 | MOY_I_Z_110 | TAW_I_Z_110 | 1 | 0.013 | 0.028 | 0.004 | 123.75 | 99
MOY(I)(Z)>TAW(I)(Z)_110L2 | MOY_I_Z_110 | TAW_I_Z_110 | 1 | 0.012 | 0.029 | 0.004 | 123.75 | 99
MP(I)(Z)>OST(I)(Z)_380L1 | MP_I_Z_380 | OST_I_Z_380 | 1 | 0.004 | 0.027 | 0.489 | 1603.75 | 1283
MP(I)(Z)>PRO(I)(Z)_220L1 | MP_I_Z_220 | PRO_I_Z_220 | 1 | 0.001 | 0.011 | 0.017 | 671.25 | 537
MP(I)(Z)>TBK(I)(T)_110L1 | MP_I_Z_110 | TBK_I_T_110 | 1 | 0.005 | 0.024 | 0.003 | 222.5 | 178
MR(I)(Z)>TBG(I)(Z)_110L1 | MR_I_Z_110 | TBG_I_Z_110 | 1 | 0.001 | 0.002 | 0.036 | 222.5 | 178
MR(I)(Z)>TBG(I)(Z)_110L2 | MR_I_Z_110 | TBG_I_Z_110 | 1 | 0.001 | 0.001 | 0.031 | 222.5 | 178
MTN(I)(Z)>MUN(I)(Z)_110L1 | MTN_I_Z_110 | MUN_I_Z_110 | 1 | 0.001 | 0.002 | 0 | 131.25 | 105
MTN(I)(Z)>MUN(I)(Z)_110L2 | MTN_I_Z_110 | MUN_I_Z_110 | 1 | 0.001 | 0.002 | 0 | 131.25 | 105
NEW(I)(Z)>BLK(I)(Z)_110L1 | NEW_I_Z_110 | BLK_I_Z_110 | 1 | 0.013 | 0.041 | 0.004 | 170 | 136
NEW(I)(Z)>PLS(I)(Z)_110L1 | NEW_I_Z_110 | PLS_I_Z_110 | 1 | 0.055 | 0.146 | 0.014 | 131.25 | 105
NEW(N)(Z)>TAN(N)(Z)_110L1 | NEW_N_Z_110 | TAN_N_Z_110 | 1 | 0.031 | 0.08 | 0.008 | 102.5 | 82
NEW(N)(Z)>TAN(N)(Z)_110L2 | NEW_N_Z_110 | TAN_N_Z_110 | 1 | 0.031 | 0.08 | 0.008 | 102.5 | 82
NQS(I)(Z)>RE(I)(Z)_110L1 | NQS_I_Z_110 | RE_I_Z_110 | 1 | 0.001 | 0.002 | 0.038 | 148.75 | 119
NW(I)(Z)>PB(I)(Z)_220L1 | NW_I_Z_220 | PB_I_Z_220 | 1 | 0 | 0.001 | 0.261 | 415 | 332
OMA(N)(Z)>STR(N)(Z)_110L1 | OMA_N_Z_110 | STR_N_Z_110 | 1 | 0.046 | 0.123 | 0.012 | 136.25 | 109
OMA(N)(Z)>STR(N)(Z)_110L2 | OMA_N_Z_110 | STR_N_Z_110 | 1 | 0.047 | 0.125 | 0.012 | 102.5 | 82
OMA(N)(Z)>TRE(N)(Z)_110L1 | OMA_N_Z_110 | TRE_N_Z_110 | 1 | 0.025 | 0.073 | 0.007 | 232.5 | 186
ONH(I)(Z)>MOY(I)(Z)_110L1 | ONH_I_Z_110 | MOY_I_Z_110 | 1 | 0.022 | 0.048 | 0.005 | 131.25 | 105
OST(I)(Z)>TYN(I)(Z)_220L1 | OST_I_Z_220 | TYN_I_Z_220 | 1 | 0.001 | 0.008 | 0.014 | 542.5 | 434
OST(I)(Z)>WOO(I)(Z)_380L1 | OST_I_Z_380 | WOO_I_Z_380 | 1 | 0.004 | 0.032 | 0.572 | 1971.25 | 1577
OUG(I)(Z)>OUG(I)(T)_110L1 | OUG_I_Z_110 | OUG_I_T_110 | 1 | 0.017 | 0.038 | 0.004 | 131.25 | 105
PA(I)(Z)>STR(I)(T)_110L1 | PA_I_Z_110 | STR_I_T_110 | 1 | 0.035 | 0.077 | 0.007 | 131.25 | 105
PB(I)(Z)>CKM(I)(Z)_220L1 | PB_I_Z_220 | CKM_I_Z_220 | 1 | 0.001 | 0.005 | 0.579 | 333.75 | 267
PB(I)(Z)>PB(I)(Z)_220L1 | PB_I_Z_220 | PB_I_Z_220 | 0 | 0 | 0.037 | 0 | 562.5 | 450
PB(I)(Z)>RE(I)(Z)_110L1 | PB_I_Z_110 | RE_I_Z_110 | 1 | 0 | 0.002 | 0.046 | 336.25 | 269
PB(I)(Z)>RE(I)(Z)_110L2 | PB_I_Z_110 | RE_I_Z_110 | 1 | 0 | 0.002 | 0.046 | 336.25 | 269
PB(I)(Z)>SHL(I)(Z)_220L1 | PB_I_Z_220 | SHL_I_Z_220 | 1 | 0 | 0.001 | 0.003 | 741.25 | 593
PLA(I)(Z)>OBE(I)(Z)_220L1 | PLA_I_Z_110 | OBE_I_Z_110 | 1 | 0.002 | 0.009 | 0.004 | 222.5 | 178
PPT(I)(Z)>PLS(I)(Z)_110L1 | PPT_I_Z_110 | PLS_I_Z_110 | 1 | 0.043 | 0.138 | 0.028 | 170 | 136
PRO(I)(Z)>TB(I)(Z)_220L1 | PRO_I_Z_220 | TB_I_Z_220 | 1 | 0.001 | 0.007 | 0.173 | 583.75 | 467
RAF(I)(Z)>RSY(I)(Z)_110L1 | RAF_I_Z_110 | RSY_I_Z_110 | 1 | 0.003 | 0.007 | 0.001 | 78.75 | 63
RAF(I)(Z)>TBG(I)(Z)_110L1 | RAF_I_Z_110 | TBG_I_Z_110 | 1 | 0.016 | 0.037 | 0.005 | 243.75 | 195
RAF(I)(Z)>TBG(I)(Z)_110L2 | RAF_I_Z_110 | TBG_I_Z_110 | 1 | 0.006 | 0.031 | 0.005 | 222.5 | 178
RE(I)(Z)>WBK(I)(Z)_110L1 | RE_I_Z_110 | WBK_I_Z_110 | 1 | 0 | 0.001 | 0.021 | 156.25 | 125
REM(I)(Z)>TRL(I)(Z)_110L1 | REM_I_Z_110 | TRL_I_Z_110 | 1 | 0.005 | 0.003 | 0.11 | 156.25 | 125
RNW(I)(Z)>DFR(I)(T)_110L1 | RNW_I_Z_110 | DFR_I_T_110 | 1 | 0.02 | 0.085 | 0.009 | 123.75 | 99
RRU(I)(Z)>SKL(I)(Z)_110L1 | RRU_I_Z_110 | SKL_I_Z_110 | 1 | 0.02 | 0.044 | 0.004 | 118.75 | 95
SBH(I)(Z)>MCE(I)(Z)_110L1 | SBH_I_Z_110 | MCE_I_Z_110 | 1 | 0.005 | 0.015 | 0.005 | 123.75 | 99
SH(I)(Z)>DAL(I)(T)_110L1 | SH_I_Z_110 | DAL_I_T_110 | 1 | 0.008 | 0.039 | 0.007 | 222.5 | 178
SH(I)(Z)>IKE(I)(T)_110L1 | SH_I_Z_110 | IKE_I_T_110 | 1 | 0.034 | 0.175 | 0.019 | 222.5 | 178
SH(I)(Z)>SOM(I)(T)_110L1 | SH_I_Z_110 | SOM_I_T_110 | 1 | 0.021 | 0.047 | 0.006 | 131.25 | 105
SLI(I)(Z)>SRA(I)(Z)_110L1 | SLI_I_Z_110 | SRA_I_Z_110 | 1 | 0.017 | 0.038 | 0.004 | 123.75 | 99
SLI(I)(Z)>SRA(I)(Z)_110L2 | SLI_I_Z_110 | SRA_I_Z_110 | 1 | 0.019 | 0.041 | 0.004 | 123.75 | 99
SOM(I)(Z)>SOM(I)(T)_110L1 | SOM_I_Z_110 | SOM_I_T_110 | 1 | 0.003 | 0.007 | 0.001 | 131.25 | 105
SOR(I)(Z)>TLK(I)(Z)_110L1 | SOR_I_Z_110 | TLK_I_Z_110 | 1 | 0.007 | 0.015 | 0.002 | 131.25 | 105
STR(I)(Z)>STR(I)(T)_110L1 | STR_I_Z_110 | STR_I_T_110 | 1 | 0.003 | 0.007 | 0.001 | 131.25 | 105
TAN(N)(Z)>TMN(N)(Z)_275L1 | TAN_N_Z_275 | TMN_N_Z_275 | 1 | 0.001 | 0.011 | 0.065 | 887.5 | 710
TAN(N)(Z)>TMN(N)(Z)_275L2 | TAN_N_Z_275 | TMN_N_Z_275 | 1 | 0.001 | 0.011 | 0.065 | 887.5 | 710
TAN(N)(Z)>WAR(N)(Z)_110L1 | TAN_N_Z_110 | WAR_N_Z_110 | 1 | 0.013 | 0.042 | 0.005 | 98.75 | 79
TAN(N)(Z)>WAR(N)(Z)_110L2 | TAN_N_Z_110 | WAR_N_Z_110 | 1 | 0.013 | 0.042 | 0.005 | 98.75 | 79
TBK(I)(Z)>TBK(I)(T)_110L1 | TBK_I_Z_110 | TBK_I_T_110 | 1 | 0.005 | 0.01 | 0.001 | 131.25 | 105
THU(I)(Z)>IKE(I)(T)_110L1 | THU_I_Z_110 | IKE_I_T_110 | 1 | 0.016 | 0.083 | 0.009 | 222.5 | 178
TRE(N)(Z)>TMN(N)(Z)_110L1 | TRE_N_Z_110 | TMN_N_Z_110 | 1 | 0.025 | 0.082 | 0.025 | 232.5 | 186
TRL(I)(Z)>OUG(I)(T)_110L1 | TRL_I_Z_110 | OUG_I_T_110 | 1 | 0.007 | 0.037 | 0.004 | 222.5 | 178
WOO(I)(Z)>PRT(I)(Z)_380L1 | WOO_I_Z_380 | PRT_I_Z_380 | 1 | 0 | 0.001 | 0.043 | 856.25 | 685
Note on H1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Unvalidated assumption of 125% of continuous rating.
Note on D6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Status to 0 if line taken to itself.
Note on F10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed from 0 to 0.0001 to allow solution.
Note on C31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Marked as LOD in TYTS, clearly linked to Lodgewood LWD).
Note on D96: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Status to 0 if line taken to itself.
Note on F109: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed from 0 to 0.0001 to allow solution.
Note on B156: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed to CTN (Cauteen)
Note on A157: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed from CBA to CBL - Cloghboola is connected to Trien (TRI), no CBA on diagram.
Note on E162: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Very small value
Note on E227: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Very small for 0 R
Note on F227: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Very small for 0 X
Note on E228: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Very small for 0 R
Note on E313: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not defined in TYTS, assumed to be no losses.
Note on F313: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not defined in TYTS, assumed to be no losses.
Note on G313: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not defined in TYTS, assumed to be no losses.
Note on I313: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not defined in TYTS, assumed to be as line from RNW
Note on C330: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Drumquin Cluster, connected to DRO and OMA
Note on D355: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Status to 0 if line taken to itself.
Note on A389: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Great Island -> Loughtown (Greenlink) Link.
Note on E389: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Equal to 0, set very small.
Note on F389: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Equal to 0, set very small.
Note on F450: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed from 0 to 0.0001 to allow solution.
Note on G514: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Assumed to be as the 1km AUG - SK line.
Note on I514: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Assumed to be as the 1km AUG - SK line.
Note on D560: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Status to 0 if line taken to itself.
Note on F563: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed from 0 to 0.0001 to allow solution.
Note on F570: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed from 0 to 0.0001 to allow solution.
Note on F591: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed from 0 to 0.0001 to allow solution.

## ts_Lmax
timestep | AA(I)(Z)>DRU(I)(Z)_110L1 | AA(I)(Z)>ENN(I)(Z)_110L1 | AA(I)(Z)>LIM(I)(Z)_110L1 | AA1(I)(Z)>SNG(I)(Z)_110L1 | AD(I)(Z)>GGO(I)(Z)_220L1 | AD(I)(Z)>KRA(I)(Z)_220L1 | AD(I)(Z)>KRA(I)(Z)_220L2 | AD(I)(Z)>LPT(I)(Z)_220L1 | AD(I)(Z)>RAF(I)(Z)_220L1 | AD(I)(Z)>WHI(I)(Z)_110L1 | ADM(I)(Z)>GCA(I)(Z)_110L1 | ADM(I)(Z)>INC(I)(Z)_110L1 | AGH(N)(Z)>ENN(N)(Z)_110L1 | AGL(I)(Z)>DYN(I)(Z)_110L1 | AGL(I)(Z)>ENN(I)(Z)_110L1 | AGN(I)(Z)>CBT(I)(Z)_110L1 | AGN(I)(Z)>CBT(I)(Z)_110L2 | AGN(I)(Z)>KSE(I)(Z)_110L1 | AGL(I)(Z)>SH(I)(Z)_110L1 | AHA(I)(Z)>KLN(I)(Z)_110L1 | ANR(I)(Z)>DOO(I)(Z)_110L1 | ANT(N)(Z)>KEL(N)(Z)_110L1 | ANT(N)(Z)>KEL(N)(Z)_110L2 | ARD(I)(Z)>TIV(I)(Z)_110L1 | ARI(I)(Z)>ARI(I)(T)_110L1 | ARK(I)(Z)>BEG(I)(Z)_110L1 | ARK(I)(Z)>BOG(I)(Z)_110L1 | ARK(I)(Z)>CKM(I)(Z)_220L1 | ARK(I)(Z)>LOD(I)(Z)_220L1 | ARK(I)(Z)>SHE(I)(Z)_110L1 | ART(I)(Z)>FIN(I)(Z)_110L1 | ART(I)(Z)>MCD(I)(Z)_110L1 | ARV(I)(Z)>COS(I)(Z)_110L1 | ARV(I)(Z)>GWE(I)(Z)_110L1 | ARV(I)(Z)>NAV(I)(Z)_110L1 | ARV(I)(Z)>SKL(I)(Z)_110L1 | ARV(I)(Z)>SKL(I)(Z)_110L2 | ATE(I)(Z)>DRO(I)(Z)_110L1 | ATE(I)(Z)>KNR(I)(Z)_110L1 | ATH(I)(Z)>LA(I)(Z)_110L1 | ATH(I)(Z)>SH(I)(Z)_110L1 | ATN(I)(Z)>INC(I)(Z)_110L1 | ATN(I)(Z)>INC(I)(Z)_110L2 | ATY(I)(Z)>CLW(I)(Z)_110L1 | ATY(I)(Z)>CNB(I)(Z)_110L1 | ATY(I)(Z)>PLS(I)(Z)_110L1 | AUG(I)(Z)>CFM(I)(Z)_110L1 | AUG(I)(Z)>CFM(I)(Z)_110L2 | AUG(I)(Z)>KPG(I)(Z)_110L1 | AUG(I)(Z)>MTN(I)(Z)_110L1 | AUG(I)(Z)>SK(I)(Z)_110L1 | AUG(I)(Z)>SK(I)(Z)_110L2 | BAL(I)(Z)>CDU(I)(Z)_110L1 | BAL(I)(Z)>DRY(I)(Z)_110L1 | BAL(I)(Z)>DEE(I)(Z)_110L1 | BAN(I)(Z)>BRI(I)(Z)_110L1 | BAN(I)(Z)>BRI(I)(Z)_110L2 | BAN(I)(Z)>DMY(I)(Z)_110L1 | BAN(I)(Z)>RAF(I)(Z)_110L1 | BAN(N)(Z)>TAN(N)(Z)_110L1 | BAN(N)(Z)>TAN(N)(Z)_110L2 | BAR(I)(Z)>BAR(I)(T)_110L1 | BCT(I)(Z)>CKM(I)(Z)_110L1 | BCT(I)(Z)>COO(I)(Z)_110L1 | BDA(I)(Z)>MON(I)(Z)_110L1 | BDA(I)(Z)>NEW(I)(Z)_110L1 | BDN(I)(Z)>CUL(I)(Z)_110L1 | BDN(I)(Z)>DOO(I)(Z)_110L1 | BEG(I)(Z)>CKM(I)(Z)_110L1 | BGH(I)(Z)>CLA(I)(Z)_110L1 | BGN(I)(Z)>MLC(I)(Z)_110L1 | BGT(I)(Z)>CNB(I)(Z)_110L1 | BGT(I)(Z)>GGT(I)(Z)_110L1 | BGT(I)(Z)>KKY(I)(Z)_110L1 | BIN(I)(Z)>CF(I)(Z)_110L1 | BIN(I)(Z)>TIV(I)(Z)_110L1 | BK(I)(Z)>CBR(I)(Z)_110L1 | BK(I)(Z)>CGW(I)(Z)_110L1 | BK(I)(Z)>MOY(I)(Z)_110L1 | BK(I)(Z)>SKY(I)(Z)_110L1 | BK(I)(Z)>SKY(I)(Z)_110L2 | BKT(I)(Z)>CUR(I)(Z)_110L1 | BKY(I)(Z)>CBT(I)(Z)_110L1 | BKY(I)(Z)>CBT(I)(Z)_110L2 | BKY(I)(Z)>KCY(I)(Z)_110 | BLA(I)(Z)>POT(I)(Z)_110L1 | BLA(I)(Z)>RE(I)(Z)_110L1 | BLC(I)(Z)>FIN(I)(Z)_220L1 | BLC(I)(Z)>SHL(I)(Z)_220L1 | BLC(I)(Z)>GRA(I)(Z)_110L1 | BLC(I)(Z)>KLM(I)(Z)_110L1 | BLC(I)(Z)>MNH(I)(Z)_110L1 | BLI(I)(Z)>DMY(I)(Z)_110L1 | BMA(N)(Z)>KEL(N)(Z)_110L1 | BMA(N)(Z)>KEL(N)(Z)_110L2 | BNH(N)(Z)>CAS(N)(Z)_110L1 | BNH(N)(Z)>CAS(N)(Z)_110L2 | BNM(N)(Z)>DON(N)(Z)_110L1 | BNM(N)(Z)>DON(N)(Z)_110L2 | BOG(I)(Z)>TTU(I)(Z)_110L1 | TTU(I)(Z)>CRA(I)(Z)_110L1 | BOL(I)(Z)>ENN(I)(Z)_110L1 | BOL(I)(Z)>TBK(I)(T)_110L1 | BPS(N)(Z)>BVG(N)(Z)_110L1 | BPS(N)(Z)>BVG(N)(Z)_110L2 | BPS(N)(Z)>BYC(N)(Z)_275L1 | BPS(N)(Z)>EDE(N)(Z)_110L1 | BPS(N)(Z)>EDE(N)(Z)_110L2 | BPS(N)(Z)>HAN(N)(Z)_275L1 | BPS(N)(Z)>KEL(N)(Z)_275L1 | BPS(N)(Z)>MAG(N)(Z)_275L1 | BRO(N)(Z)>RSK(N)(Z)_110L1 | BRY(I)(Z)>RAF(I)(Z)_110L1 | BRY(I)(Z)>RAF(I)(Z)_110L2 | BTN(I)(Z)>CLE(I)(Z)_220L1 | BTN(I)(Z)>CLE(I)(Z)_220L2 | BUT(I)(Z)>CUL(I)(Z)_110L1 | BUT(I)(Z)>KTN(I)(Z)_110L1 | BVG(N)(Z)>KEL(N)(Z)_110L1 | BVG(N)(Z)>KEL(N)(Z)_110L2 | BVG(N)(Z)>LAR(N)(Z)_110L1 | BVG(N)(Z)>LAR(N)(Z)_110L2 | BVK(I)(Z)>BYH(I)(Z)_220L1 | BVK(I)(Z)>CLA(I)(Z)_220L1 | BVK(I)(Z)>CTG(I)(Z)_110L1 | BWR(I)(Z)>CRA(I)(Z)_110L1 | BYH(I)(Z)>CDL(I)(Z)_110L1 | BYH(I)(Z)>GLE(I)(Z)_110L1 | CAB(I)(Z)>PTN(I)(Z)_110L1 | CAB(I)(Z)>WOL(I)(Z)_110L1 | CAH(I)(Z)>BAR(I)(T)_110L1 | CAH(I)(Z)>DOO(I)(Z)_110L1 | CAH(I)(Z)>KHL(I)(Z)_110L1 | CAH(I)(Z)>TIP(I)(Z)_110L1 | CAR(N)(Z)>CAS(N)(Z)_110L1 | CAR(N)(Z)>CAS(N)(Z)_110L2 | CAR(N)(Z)>EDE(N)(Z)_110L1 | CAR(N)(Z)>EDE(N)(Z)_110L2 | CAS(N)(Z)>CRE(N)(Z)_110L1 | CAS(N)(Z)>CRE(N)(Z)_110L2 | CAS(N)(Z)>HAN(N)(Z)_275L1 | CAS(N)(Z)>HAN(N)(Z)_275L2 | CAS(N)(Z)>KNO(N)(Z)_110L1 | CAS(N)(Z)>KNO(N)(Z)_110L2 | CAS(N)(Z)>KPS(N)(Z)_275L1 | CAS(N)(Z)>NAR(N)(Z)_110L1 | CAS(N)(Z)>NAR(N)(Z)_110L2 | CAS(N)(Z)>RAT(N)(Z)_110L1 | CAS(N)(Z)>RAT(N)(Z)_110L2 | CAS(N)(Z)>ROS(N)(Z)_110L1 | CAS(N)(Z)>ROS(N)(Z)_110L2 | CAS(N)(Z)>TAN(N)(Z)_275L1 | CTN(I)(Z)>KLN(I)(Z)_110L1 | CBL(I)(Z)>TRI(I)(Z)_110L1 | CBG(I)(Z)>CBR(I)(Z)_110L1 | CBR(I)(Z)>CLN(I)(Z)_110L1 | CBR(I)(Z)>DLT(I)(Z)_110L1 | CBT(I)(Z)>INC(I)(Z)_220L1 | CBT(I)(Z)>KCY(I)(Z)_110L1 | CBT(I)(Z)>INC(I)(Z)_220L2 | CBT(I)(Z)>MAY(I)(Z)_220L1 | CBT(I)(Z)>MAY(I)(Z)_220L2 | CD(I)(Z)>KBY(I)(Z)_110L1 | CD(I)(Z)>MAC(I)(Z)_110L1 | CDK(I)(Z)>LWD(I)(Z)_110L1 | CDU(I)(Z)>FIN(I)(Z)_220L1 | CDU(I)(Z)>FIN(I)(Z)_220L2 | CDU(I)(Z)>HN(I)(Z)_220L1 | CDU(I)(Z)>BLU(I)(Z)_110L1 | CDU(I)(Z)>GLN(I)(Z)_110L1 | BLU(I)(Z)>MUL(I)(Z)_110L1 | CDU(I)(Z)>PLA(I)(Z)_110L1 | CDU(I)(Z)>RYB(I)(Z)_110L1 | CDU(I)(Z)>SBH(I)(Z)_110L1 | CDU(I)(Z)>WOO(I)(Z)_220L1 | CDY(I)(Z)>ARI(I)(T)_110L1 | CDY(I)(Z)>GRV(I)(Z)_110L1 | CDY(I)(Z)>SRA(I)(Z)_110L1 | CEN(N)(Z)>CRE(N)(Z)_110L1 | CEN(N)(Z)>CRE(N)(Z)_110L2 | CF(I)(Z)>CAD(Y)(Z)_110L1 | CF(I)(Z)>CKL(Y)(Z)_110L1 | CF(I)(Z)>CL(I)(Z)_110L1 | CF(I)(Z)>CLO(I)(Z)_110L1 | CF(I)(Z)>CLO(I)(Z)_110L2 | CF(I)(Z)>COR(I)(Z)_110L1 | CF(I)(Z)>SRA(I)(Z)_110L1 | CF(I)(Z)>SRA(I)(Z)_110L2 | CFD(I)(Z)>MUL(I)(Z)_110L1 | CFD(I)(Z)>KIN(I)(Z)_110L1 | CGL(I)(Z)>GAE(I)(Z)_110L1 | CHA(I)(Z)>GLE(I)(Z)_110L1 | CHA(I)(Z)>KLN(I)(Z)_110L1 | CHA(I)(Z)>MAL(I)(Z)_110L1 | CHE(I)(Z)>FAS(I)(Z)_110L1 | CKG(I)(Z)>CBT(I)(Z)_110L1 | CKG(I)(Z)>CBT(I)(Z)_110L2 | CKG(I)(Z)>KUD(I)(Z)_110L1 | CKM(I)(Z)>CHE(I)(Z)_110L1 | CKM(I)(Z)>COO(I)(Z)_110L1 | CKM(I)(Z)>DSN(I)(Z)_220L1 | CKM(I)(Z)>FAS(I)(Z)_110L1 | CKM(I)(Z)>FAS(I)(Z)_110L2 | CKM(I)(Z)>ISH(I)(Z)_220L1 | CKM(I)(Z)>POT(I)(Z)_110L1 | CKN(I)(Z)>CGL(I)(Z)_110L1 | CKN(I)(Z)>GRO(I)(Z)_110L1 | CKN(I)(Z)>KER(I)(Z)_110L1 | CLA(I)(Z)>CKN(I)(Z)_110L1 | CLA(I)(Z)>DMY(I)(Z)_110L1 | CLA(I)(Z)>KRA(I)(Z)_220L1 | CLA(I)(Z)>MAC(I)(Z)_110L1 | CLA(I)(Z)>MAC(I)(Z)_110L2 | CLE(I)(Z)>CDU(I)(Z)_220L1 | CLE(I)(Z)>WOO(I)(Z)_220L1 | CLG(I)(Z)>CDU(I)(Z)_110L1 | CLG(I)(Z)>FIN(I)(Z)_110L1 | CLH(I)(Z)>TRI(I)(Z)_110L1 | CLH(I)(Z)>TRL(I)(Z)_110L1 | CLN(I)(Z)>LA(I)(Z)_110L1 | CLO(I)(Z)>CF(I)(Z)_110L1 | CLO(I)(Z)>GOL(I)(T)_110L1 | CLO(I)(Z)>MRY(I)(Z)_110L1 | CLU(I)(Z)>CBT(I)(Z)_110L1 | CLU(I)(Z)>KUD(I)(Z)_110L1 | CLW(I)(Z)>KLS(I)(Z)_110L1 | CLW(I)(Z)>KLS(I)(Z)_110L2 | CLW(I)(Z)>STR(I)(T)_110L1 | CNB(I)(Z)>GGT(I)(T)_110L1 | CNB(I)(Z)>PLS(I)(T)_110L1 | CNB(I)(Z)>MP(I)(T)_380L1 | CNB(I)(Z)>DSN(I)(T)_380L1 | COL(I)(Z)>CDU(I)(Z)_110L1 | COL(I)(Z)>FIN(I)(Z)_110L1 | COL(N)(Z)>CPS(N)(Z)_110L1 | COL(N)(Z)>LIM(N)(Z)_110L1 | COL(N)(Z)>LOG(N)(Z)_110L1 | COL(N)(Z)>LOG(N)(Z)_110L2 | COL(N)(Z)>RSK(N)(Z)_110L1 | COO(I)(Z)>FTT(I)(Z)_110L1 | COO(I)(Z)>INC(I)(Z)_110L1 | COR(I)(Z)>ENN(N)(Z)_110L1 | COR(I)(Z)>GWE(I)(Z)_110L1 | COS(I)(Z)>ARI(I)(T)_110L1 | COS(I)(Z)>FLA(I)(Z)_110L1 | COS(I)(Z)>FLA(I)(Z)_110L2 | COW(I)(Z)>OLD(I)(Z)_110L1 | COW(I)(Z)>OLD(I)(Z)_110L2 | COW(I)(Z)>RAF(I)(Z)_110L1 | COW(I)(Z)>WHI(I)(Z)_110L1 | CPK(I)(Z)>CKM(I)(Z)_110L1 | CPK(I)(Z)>TNY(I)(Z)_110L1 | CPS(N)(Z)>CRD(N)(Z)_110L1 | CPS(N)(Z)>KMT(N)(Z)_110L1 | CPS(N)(Z)>LIM(N)(Z)_110L1 | CPS(N)(Z)>LMR(N)(Z)_110L1 | CPS(N)(Z)>LMR(N)(Z)_110L2 | CPS(N)(Z)>MAG(N)(Z)_275L1 | CPS(N)(Z)>MAG(N)(Z)_275L2 | CPS(N)(Z)>SPR(N)(Z)_110L1 | CPS(N)(Z)>SPR(N)(Z)_110L2 | CPS(N)(Z)>STR(N)(Z)_110L1 | CRA(I)(Z)>LWD(I)(Z)_110L1 | CRA(I)(Z)>WEX(I)(Z)_110L1 | CRG(N)(Z)>KEL(N)(Z)_110L1 | CRG(N)(Z)>TMN(N)(Z)_110L1 | CRM(I)(Z)>KLM(I)(Z)_110L1 | CRM(I)(Z)>KLM(I)(Z)_110L2 | CRO(I)(Z)>IA(I)(Z)_110L1 | CRO(I)(Z)>KBY(I)(Z)_110L1 | CSH(I)(Z)>CLN(I)(Z)_110L1 | CSH(I)(Z)>DLT(I)(Z)_110L1 | CSH(I)(Z)>ENN(I)(Z)_110L1 | CSH(I)(Z)>FLA(I)(Z)_220L1 | CSH(I)(Z)>GAL(I)(Z)_110L1 | CSH(I)(Z)>GAL(I)(Z)_110L2 | CSH(I)(Z)>GAL(I)(Z)_110L3 | CSH(I)(Z)>PRO(I)(Z)_220L1 | CSH(I)(Z)>SAL(I)(Z)_110L1 | CSH(I)(Z)>SOM(I)(T)_110L1 | CSH(I)(Z)>TYN(I)(Z)_220L1 | CTN(I)(Z)>TIP(I)(Z)_110L1 | CTY(I)(Z)>FTT(I)(Z)_110L1 | CTY(I)(Z)>INC(I)(Z)_110L1 | CUL(I)(Z)>DGN(I)(Z)_110L1 | CUL(I)(Z)>GI(I)(Z)_220L1 | CUL(I)(Z)>KRA(I)(Z)_220L1 | CUL(I)(Z)>WAT(I)(Z)_110L1 | CUL(I)(Z)>RTO(I)(Z)_110L1 | CUN(I)(Z)>GLR(I)(Z)_110L1 | CUN(I)(Z)>SLI(I)(Z)_110L1 | CUR(I)(Z)>BKM(I)(Z)_110L1 | CUR(I)(Z)>NEN(I)(Z)_110L1 | CUS(I)(Z)>MLC(I)(Z)_110L1 | CUS(I)(Z)>NEW(I)(Z)_110L1 | CUS(I)(Z)>PLS(I)(Z)_110L1 | CUS(I)(Z)>PPT(I)(Z)_110L1 | CVW(I)(Z)>COW(I)(Z)_110L1 | CVW(I)(Z)>DKL(I)(Z)_110L1 | CVW(I)(Z)>KRA(I)(Z)_110L1 | DAL(I)(Z)>DAL(I)(T)_110L1 | DDK(I)(Z)>LOU(I)(Z)_110L1 | DDK(I)(Z)>MLN(I)(Z)_110L1 | DER(I)(Z)>KIN(I)(Z)_110L1 | DER(I)(Z)>TEN(I)(Z)_110L1 | TEN(I)(Z)>MAY(I)(Z)_110L1 | DER(I)(Z)>TSB(I)(Z)_110L1 | DEY(I)(Z)>DAL(I)(T)_110L1 | DEY(I)(Z)>PLS(I)(Z)_110L1 | DFR(I)(T)>DFR(I)(Z)_110L1 | DFR(I)(Z)>MGT(I)(Z)_110L1 | DGN(I)(Z)>WHE(I)(Z)_110L1 | DGN(I)(Z)>RTO(I)(Z)_110L1 | DMY(I)(Z)>CDN(I)(Z)_110L1 | DMY(I)(Z)>MAC(I)(Z)_110L1 | DON(N)(Z)>FIN(N)(Z)_110L1 | DON(N)(Z)>FIN(N)(Z)_110L2 | DON(N)(Z)>HAN(N)(Z)_110L1 | DON(N)(Z)>HAN(N)(Z)_110L2 | DRM(I)(Z)>CLO(I)(Z)_110L1 | DRM(I)(Z)>LET(I)(Z)_110L1 | DRM(I)(Z)>MEE(I)(Z)_110L1 | DRO(N)(Z)>ENN(N)(Z)_110L1 | DRO(N)(Z)>ENN(N)(Z)_110L2 | DRO(N)(Z)>OMA(N)(Z)_110L1 | DRO(N)(Z)>OMA(N)(Z)_110L2 | DRQ(N)(Z)>DRO(N)(Z)_110L1 | DRU(I)(Z)>ENN(I)(Z)_110L1 | DRU(N)(Z)>TAN(N)(Z)_110L1 | DRU(N)(Z)>TAN(N)(Z)_110L2 | DRU(N)(Z)>TAN(N)(Z)_110L3 | DRU(N)(Z)>TMN(N)(Z)_110L1 | DRU(N)(Z)>TMN(N)(Z)_110L2 | DRY(I)(Z)>GOR(I)(Z)_110L1 | DRY(I)(Z)>LOU(I)(Z)_110L1 | DRY(I)(Z)>PLA(I)(Z)_110L1 | DRY(I)(Z)>OBE(I)(Z)_110L1 | DSN(I)(Z)>KLS(I)(Z)_220L1 | DSN(I)(Z)>MAY(I)(Z)_220L1 | DSN(I)(Z)>MAY(I)(Z)_220L2 | DSN(I)(Z)>MAY(I)(Z)_220L3 | DSN(I)(Z)>MP(I)(Z)_380L1 | DSN(I)(Z)>TH(I)(Z)_220L1 | DTN(I)(Z)>BLC(I)(Z)_110L1 | DTN(I)(Z)>FIN(I)(Z)_110L1 | DTN(I)(Z)>KLM(I)(Z)_110L1 | DUN(N)(Z)>OMA(N)(Z)_110L1 | DUN(N)(Z)>TMN(N)(Z)_110L1 | DUN(N)(Z)>TMN(N)(Z)_110L2 | DUN(N)(Z)>TMN(N)(Z)_110L3 | ENN(I)(Z)>SLC(I)(Z)_110L1 | FIN(I)(Z)>GLA(I)(Z)_110L1 | FIN(I)(Z)>GRA(I)(Z)_110L1 | FIN(I)(Z)>HN(I)(Z)_220L1 | FIN(I)(Z)>MCD(I)(Z)_110L1 | FIN(I)(Z)>NW(I)(Z)_220L1 | FIN(I)(Z)>POP(I)(Z)_110L1 | FIN(I)(Z)>PTN(I)(Z)_110L1 | FIN(I)(Z)>SHL(I)(Z)_220L1 | FIN(I)(Z)>SVN(I)(Z)_110L1 | FIN(N)(Z)>HAN(N)(Z)_110L1 | FIN(N)(Z)>HAN(N)(Z)_110L2 | FLA(I)(Z)>GIL(I)(Z)_110L1 | FLA(I)(Z)>LOU(I)(Z)_220L1 | FLA(I)(Z)>SLB(I)(Z)_110L1 | FLA(I)(Z)>SLI(I)(Z)_110L1 | FLA(I)(Z)>SRA(I)(Z)_220L1 | FLA(I)(Z)>TON(I)(Z)_110L1 | FRS(I)(Z)>HAR(I)(Z)_110L1 | FRS(I)(Z)>HEU(I)(Z)_110L1 | FRS(I)(Z)>INC(I)(Z)_110L1 | FRS(I)(Z)>TRN(I)(Z)_110L1 | GAL(I)(Z)>SAL(I)(Z)_110L1 | GAL(I)(Z)>SEE(I)(Z)_110L1 | CDU(I)(Z)>GAN(I)(Z)_110L1 | GCA(I)(Z)>GRI(I)(T)_110L1 | GCA(I)(Z)>INC(I)(Z)_110L1 | GCA(I)(Z)>INC(I)(Z)_110L2 | GCA(I)(Z)>NAN(I)(Z)_110L1 | GCA(I)(Z)>NAN(I)(Z)_110L2 | GGO(I)(Z)>RAF(I)(Z)_220L1 | GI(I)(Z)>KKY(I)(Z)_110L1 | GI(I)(Z)>KLS(I)(Z)_220L1 | GI(I)(Z)>LWD(I)(Z)_220L1 | GI(I)(Z)>LWN(I)(Z)_220L1 | GI(I)(Z)>WAT(I)(Z)_110L1 | GI(I)(Z)>WAT(I)(Z)_110L2 | GI(I)(Z)>ROP(I)(Z)_110L1 | ROP(I)(Z)>WEX(I)(Z)_110L1 | GLA(I)(Z)>SVN(I)(Z)_110L1 | GLE(I)(Z)>KCR(I)(Z)_110L1 | GLE(N)(Z)>KEL(N)(Z)_110L1 | GLE(N)(Z)>KEL(N)(Z)_110L2 | GOL(I)(Z)>GOL(I)(T)_110L1 | GOR(I)(Z)>LOU(I)(Z)_220L1 | GOR(I)(Z)>MAY(I)(Z)_220L1 | GOR(I)(Z)>MTH(I)(Z)_110L1 | GOR(I)(Z)>NAV(I)(Z)_110L1 | GOR(I)(Z)>NAV(I)(Z)_110L2 | GOR(I)(Z)>NAV(I)(Z)_110L3 | GOR(I)(Z)>GRH(I)(Z)_110L1 | GRH(I)(Z)>PLA(I)(Z)_110L1 | GOR(N)(Z)>OMA(N)(Z)_110L1 | GOR(N)(Z)>TMN(N)(Z)_110L1 | GRA(I)(Z)>NBY(I)(Z)_110L1 | GRI(I)(T)>MAY(I)(Z)_110L1 | GRI(I)(Z)>GRI(I)(T)_110L1 | GRO(I)(Z)>BVK(I)(Z)_110L1 | HAN(N)(Z)>BYC(N)(Z)_275L1 | HAN(N)(Z)>LIS(N)(Z)_110L1 | HAN(N)(Z)>LIS(N)(Z)_110L2 | HAR(I)(Z)>RE(I)(Z)_110L1 | HEU(I)(Z)>INC(I)(Z)_110L1 | HWN(I)(Z)>MGT(I)(Z)_110L1 | HWN(I)(Z)>KIN(I)(Z)_110L1 | HWN(I)(Z)>DFR(I)(T)_110L1 | IA(I)(Z)>MAC(I)(Z)_110L1 | IKE(I)(Z)>IKE(I)(T)_110L1 | INC(I)(Z)>ISH(I)(Z)_220L1 | INC(I)(Z)>MIL(I)(Z)_110L1 | INC(I)(Z)>PB(I)(Z)_220L1 | INC(I)(Z)>PB(I)(Z)_220L2 | ISH(I)(Z)>SHL(I)(Z)_220L1 | KBY(I)(Z)>KRA(I)(Z)_110L1 | KBY(I)(Z)>KRA(I)(Z)_110L2 | KBY(I)(Z)>MAL(I)(Z)_110L1 | KBY(I)(Z)>MR(I)(Z)_110L1 | KBY(I)(Z)>MR(I)(Z)_110L2 | KEL(N)(Z)>KPS(N)(Z)_275L1 | KEL(N)(Z)>KPS(N)(Z)_275L2 | KEL(N)(Z)>MAG(N)(Z)_275L1 | KEL(N)(Z)>RSK(N)(Z)_110L1 | KER(I)(Z)>OUG(I)(T)_110L1 | KIN(I)(Z)>DFR(I)(T)_110L1 | KIN(I)(Z)>MUL(I)(Z)_110L1 | KLH(I)(Z)>THU(I)(Z)_110L1 | KLM(I)(Z)>NBY(I)(Z)_110L1 | KLM(I)(Z)>POP(I)(Z)_110L1 | KLN(I)(Z)>CUR(I)(Z)_110L1 | KLN(I)(Z)>KPG(I)(Z)_220L1 | KLN(I)(Z)>KRA(I)(Z)_220L1 | KLN(I)(Z)>LIM(I)(Z)_110L1 | KLN(I)(Z)>LIM(I)(Z)_110L2 | KLN(I)(Z)>SH(I)(Z)_220L1 | KLN(I)(Z)>SNG(I)(Z)_110L1 | KLP(I)(Z)>CNG(I)(Z)_110L1 | KLP(I)(Z)>KNR(I)(Z)_110L1 | KLP(I)(Z)>KNR(I)(Z)_220L1 | KLP(I)(Z)>KNR(I)(Z)_220L2 | KLP(I)(Z)>MP(I)(Z)_220L1 | KLP(I)(Z)>MP(I)(Z)_220L2 | KLP(I)(Z)>RAT(I)(Z)_110L1 | KLP(I)(Z)>TB(I)(Z)_110L1 | KLP(I)(Z)>TB(I)(Z)_110L2 | KLP(I)(Z)>TB(I)(Z)_220L1 | KLP(I)(Z)>TB(I)(Z)_220L2 | KLP(I)(Z)>TRL(I)(Z)_110L1 | KLP(I)(Z)>TRL(I)(Z)_110L2 | KLS(I)(Z)>KKY(I)(Z)_110L1 | KMT(N)(Z)>SLK(N)(Z)_110L1 | KMT(N)(Z)>STR(N)(Z)_110L1 | KNR(I)(Z)>BYH(I)(Z)_220L1 | KNR(I)(Z)>TRI(I)(Z)_110L1 | KNR(I)(Z)>TRI(I)(Z)_110L2 | KNY(I)(Z)>BUF(I)(Z)_110L1 | KNY(I)(Z)>KLH(I)(Z)_110L1 | KNY(I)(Z)>SAL(I)(Z)_110L1 | KNY(I)(Z)>SCR(I)(Z)_110L1 | KNY(I)(Z)>UGL(I)(Z)_110L1 | KPS(N)(Z)>TAN(N)(Z)_275L1 | KRA(I)(Z)>BAR(I)(T)_110L1 | KRA(I)(Z)>LGT(I)(T)_110L1 | KRA(I)(Z)>MEN(I)(Z)_110L1 | KRA(I)(Z)>MID(I)(Z)_110L1 | KRA(I)(Z)>RAF(I)(Z)_220L1 | KRA(I)(Z)>WHO(I)(Z)_110L1 | KTL(I)(Z)>MAY(I)(Z)_110L1 | KTL(I)(Z)>MON(I)(Z)_110L1 | KTN(I)(Z)>WAT(I)(Z)_110L1 | KUD(I)(Z)>CBT(I)(Z)_110L1 | KUR(I)(Z)>NAV(I)(Z)_110L1 | KYT(I)(Z)>MAY(I)(Z)_220L1 | KYT(I)(Z)>WOO(I)(Z)_220L1 | LA(I)(Z)>MUL(I)(Z)_110L1 | LA(I)(Z)>RIC(I)(Z)_110L1 | LA(I)(Z)>RIC(I)(Z)_110L2 | LA(I)(Z)>SLB(I)(Z)_110L1 | LNA(I)(Z)>TIV(I)(Z)_110L1 | LCK(I)(Z)>MUL(I)(Z)_110L1 | LET(I)(Z)>GOL(I)(T)_110L1 | LET(I)(Z)>STR(N)(Z)_110L1 | LET(I)(Z)>TIV(I)(Z)_110L1 | LET(I)(Z)>TLK(I)(Z)_110L1 | LET(I)(Z)>LNA(I)(Z)_110L1 | LIB(I)(Z)>MR(I)(Z)_110L1 | LIB(I)(Z)>MR(I)(Z)_110L2 | LIM(I)(Z)>MTN(I)(Z)_110L1 | LIM(I)(Z)>RAT(I)(Z)_110L1 | LIS(I)(Z)>LOU(I)(Z)_110L1 | LIS(I)(Z)>LSA(I)(T)_110L1 | LSA(I)(T)>SKL(I)(Z)_110L1 | LIS(N)(Z)>TAN(N)(Z)_110L1 | LIS(N)(Z)>TAN(N)(Z)_110L2 | LOU(I)(Z)>MLN(I)(Z)_110L1 | LOU(I)(Z)>MTH(I)(Z)_110L1 | LOU(I)(Z)>RRU(I)(Z)_110L1 | LOU(I)(Z)>TAN(N)(Z)_275L1 | LOU(I)(Z)>TAN(N)(Z)_275L2 | LOU(I)(Z)>WOO(I)(Z)_220L1 | LSA(I)(Z)>LSA(I)(T)_110L1 | LSN(I)(Z)>THU(I)(Z)_110L1 | MAG(N)(Z)>TMN(N)(Z)_275L1 | MAG(N)(Z)>TMN(N)(Z)_275L2 | MAY(I)(Z)>BLK(I)(Z)_110L1 | MAY(I)(Z)>GRI(I)(Z)_110L1 | MAY(I)(Z)>RNW(I)(Z)_110L1 | MAY(I)(Z)>RYB(I)(Z)_110L1 | MAY(I)(Z)>SH(I)(Z)_220L1 | MAY(I)(Z)>TH(I)(Z)_220L1 | MAY(I)(Z)>WOO(I)(Z)_220L1 | MCD(I)(Z)>NQS(I)(Z)_110L1 | MCD(I)(Z)>WOL(I)(Z)_110L1 | MHL(I)(Z)>RE(I)(Z)_110L1 | MHL(I)(Z)>TRN(I)(Z)_110L1 | MID(I)(Z)>WHI(I)(Z)_110L1 | MID(I)(Z)>LGT(I)(Z)_110L1 | MIL(I)(Z)>RE(I)(Z)_110L1 | MIL(I)(Z)>RE(I)(Z)_110L2 | MKL(N)(Z)>OMA(N)(Z)_110L1 | MLC(I)(Z)>TSB(I)(Z)_110L1 | MNH(I)(Z)>MTA(I)(Z)_110L1 | MOY(I)(Z)>TAW(I)(Z)_110L1 | MOY(I)(Z)>TAW(I)(Z)_110L2 | MP(I)(Z)>OST(I)(Z)_380L1 | MP(I)(Z)>PRO(I)(Z)_220L1 | MP(I)(Z)>TBK(I)(T)_110L1 | MR(I)(Z)>TBG(I)(Z)_110L1 | MR(I)(Z)>TBG(I)(Z)_110L2 | MTN(I)(Z)>MUN(I)(Z)_110L1 | MTN(I)(Z)>MUN(I)(Z)_110L2 | NEW(I)(Z)>BLK(I)(Z)_110L1 | NEW(I)(Z)>PLS(I)(Z)_110L1 | NEW(N)(Z)>TAN(N)(Z)_110L1 | NEW(N)(Z)>TAN(N)(Z)_110L2 | NQS(I)(Z)>RE(I)(Z)_110L1 | NW(I)(Z)>PB(I)(Z)_220L1 | OMA(N)(Z)>STR(N)(Z)_110L1 | OMA(N)(Z)>STR(N)(Z)_110L2 | OMA(N)(Z)>TRE(N)(Z)_110L1 | ONH(I)(Z)>MOY(I)(Z)_110L1 | OST(I)(Z)>TYN(I)(Z)_220L1 | OST(I)(Z)>WOO(I)(Z)_380L1 | OUG(I)(Z)>OUG(I)(T)_110L1 | PA(I)(Z)>STR(I)(T)_110L1 | PB(I)(Z)>CKM(I)(Z)_220L1 | PB(I)(Z)>RE(I)(Z)_110L1 | PB(I)(Z)>RE(I)(Z)_110L2 | PB(I)(Z)>SHL(I)(Z)_220L1 | PLA(I)(Z)>OBE(I)(Z)_220L1 | PPT(I)(Z)>PLS(I)(Z)_110L1 | PRO(I)(Z)>TB(I)(Z)_220L1 | RAF(I)(Z)>RSY(I)(Z)_110L1 | RAF(I)(Z)>TBG(I)(Z)_110L1 | RAF(I)(Z)>TBG(I)(Z)_110L2 | RE(I)(Z)>WBK(I)(Z)_110L1 | REM(I)(Z)>TRL(I)(Z)_110L1 | RNW(I)(Z)>DFR(I)(T)_110L1 | RRU(I)(Z)>SKL(I)(Z)_110L1 | SBH(I)(Z)>MCE(I)(Z)_110L1 | SH(I)(Z)>DAL(I)(T)_110L1 | SH(I)(Z)>IKE(I)(T)_110L1 | SH(I)(Z)>SOM(I)(T)_110L1 | SLI(I)(Z)>SRA(I)(Z)_110L1 | SLI(I)(Z)>SRA(I)(Z)_110L2 | SOM(I)(Z)>SOM(I)(T)_110L1 | SOR(I)(Z)>TLK(I)(Z)_110L1 | STR(I)(Z)>STR(I)(T)_110L1 | TAN(N)(Z)>TMN(N)(Z)_275L1 | TAN(N)(Z)>TMN(N)(Z)_275L2 | TAN(N)(Z)>WAR(N)(Z)_110L1 | TAN(N)(Z)>WAR(N)(Z)_110L2 | TBK(I)(Z)>TBK(I)(T)_110L1 | THU(I)(Z)>IKE(I)(T)_110L1 | TRE(N)(Z)>TMN(N)(Z)_110L1 | TRL(I)(Z)>OUG(I)(T)_110L1 | WOO(I)(Z)>PRT(I)(Z)_380L1
t-1 | 99 | 99 | 178 | 145 | 536 | 393 | 393 | 593 | 434 | 99 | 140 | 103 | 109 | 105 | 99 | 187 | 187 | 187 | 104 | 112 | 105 | 82 | 82 | 105 | 105 | 99 | 178 | 434 | 434 | 34 | 120 | 120 | 104 | 178 | 178 | 178 | 178 | 120 | 178 | 99 | 178 | 140 | 140 | 99 | 105 | 99 | 96 | 96 | 178 | 178 | 120 | 120 | 178 | 178 | 178 | 105 | 99 | 99 | 99 | 82 | 82 | 136 | 140 | 130 | 99 | 122 | 196 | 178 | 136 | 178 | 124 | 178 | 178 | 178 | 99 | 136 | 195 | 178 | 178 | 192 | 187 | 120 | 187 | 187 | 187 | 119 | 119 | 570 | 570 | 140 | 140 | 842 | 105 | 109 | 109 | 82 | 82 | 75 | 75 | 178 | 178 | 178 | 178 | 82 | 82 | 710 | 69 | 70 | 710 | 710 | 710 | 144 | 63 | 99 | 570 | 570 | 178 | 200 | 109 | 109 | 79 | 79 | 434 | 740 | 228 | 115 | 195 | 124 | 80 | 120 | 105 | 178 | 178 | 178 | 69 | 70 | 69 | 69 | 132 | 132 | 710 | 710 | 66 | 66 | 710 | 109 | 109 | 82 | 82 | 144 | 144 | 710 | 178 | 124 | 99 | 99 | 99 | 761 | 187 | 761 | 761 | 761 | 178 | 178 | 115 | 434 | 434 | 555 | 123 | 178 | 130 | 178 | 103 | 238 | 434 | 178 | 132 | 178 | 144 | 144 | 140 | 140 | 136 | 178 | 178 | 178 | 196 | 178 | 178 | 178 | 130 | 99 | 136 | 178 | 105 | 187 | 187 | 187 | 105 | 130 | 434 | 105 | 105 | 593 | 119 | 178 | 120 | 178 | 178 | 178 | 646 | 161 | 161 | 434 | 434 | 187 | 124 | 99 | 105 | 63 | 178 | 187 | 136 | 187 | 187 | 99 | 99 | 105 | 178 | 178 | 1577 | 1577 | 143 | 104 | 82 | 82 | 82 | 82 | 186 | 124 | 136 | 99 | 178 | 178 | 99 | 99 | 105 | 105 | 99 | 99 | 100 | 100 | 200 | 143 | 82 | 82 | 82 | 412 | 412 | 82 | 82 | 109 | 178 | 99 | 82 | 109 | 140 | 140 | 196 | 178 | 178 | 99 | 178 | 350 | 99 | 99 | 99 | 392 | 97 | 99 | 761 | 178 | 124 | 103 | 178 | 746 | 646 | 178 | 178 | 178 | 178 | 190 | 105 | 136 | 134 | 136 | 136 | 99 | 105 | 99 | 105 | 99 | 99 | 99 | 74 | 74 | 99 | 178 | 178 | 99 | 104 | 178 | 178 | 211 | 196 | 69 | 69 | 144 | 144 | 103 | 99 | 99 | 82 | 82 | 82 | 82 | 82 | 99 | 79 | 79 | 108 | 109 | 109 | 99 | 99 | 99 | 178 | 393 | 350 | 350 | 434 | 1283 | 351 | 140 | 140 | 140 | 186 | 157 | 144 | 186 | 195 | 105 | 119 | 593 | 119 | 332 | 120 | 80 | 536 | 105 | 144 | 144 | 105 | 384 | 99 | 99 | 434 | 98 | 107 | 140 | 107 | 140 | 99 | 99 | 178 | 103 | 103 | 103 | 120 | 120 | 570 | 99 | 393 | 434 | 593 | 178 | 178 | 178 | 178 | 136 | 122 | 82 | 82 | 105 | 434 | 350 | 99 | 99 | 99 | 99 | 99 | 99 | 200 | 200 | 119 | 105 | 105 | 195 | 710 | 82 | 80 | 107 | 140 | 136 | 136 | 104 | 196 | 80 | 562 | 120 | 267 | 351 | 593 | 178 | 99 | 134 | 103 | 103 | 710 | 710 | 710 | 185 | 178 | 99 | 178 | 178 | 119 | 120 | 136 | 434 | 512 | 99 | 80 | 269 | 178 | 140 | 136 | 731 | 731 | 660 | 660 | 136 | 99 | 99 | 350 | 350 | 99 | 178 | 99 | 109 | 143 | 434 | 178 | 99 | 140 | 190 | 195 | 135 | 195 | 710 | 136 | 105 | 124 | 99 | 353 | 178 | 99 | 136 | 99 | 187 | 99 | 761 | 761 | 99 | 99 | 99 | 99 | 136 | 124 | 99 | 99 | 136 | 105 | 136 | 100 | 99 | 178 | 99 | 99 | 99 | 99 | 82 | 80 | 99 | 99 | 95 | 710 | 710 | 350 | 120 | 104 | 710 | 710 | 99 | 99 | 80 | 178 | 269 | 325 | 350 | 119 | 120 | 140 | 140 | 99 | 105 | 100 | 120 | 139 | 135 | 190 | 99 | 99 | 1283 | 537 | 178 | 178 | 178 | 105 | 105 | 136 | 105 | 82 | 82 | 119 | 332 | 109 | 82 | 186 | 105 | 434 | 1577 | 105 | 105 | 267 | 269 | 269 | 593 | 178 | 136 | 467 | 63 | 195 | 178 | 125 | 125 | 99 | 95 | 99 | 178 | 178 | 105 | 99 | 99 | 105 | 105 | 105 | 710 | 710 | 79 | 79 | 105 | 178 | 186 | 178 | 685
Note on EO1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed from CBA to CBL - Cloghboola is connected to Trien (TRI), no CBA on diagram.
Note on MU1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Great Island -> Loughtown (Greenlink) Link.
Note on RD2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Limited to 450 MW total flow North to South or South to North in line with S_MWR_ROI.
Note on RE2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Limited to 450 MW total flow North to South or South to North in line with S_MWR_ROI.
Note on RG2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Assumed to be as the 1km AUG - SK line.

## transformer
name | from_busname | to_busname | type | stat | r | x | b | ShortTermRating | ContinousRating
AD_T2101 | AD_I_Z_220 | AD_I_Z_110 | 1 | 2 | 0.001 | 0.124 | 0 | 156.25 | 125
ARK_T2101 | ARK_I_Z_220 | ARK_I_Z_110 | 1 | 2 | 0.007 | 0.18 | 0 | 78.75 | 63
ARK_T2102 | ARK_I_Z_220 | ARK_I_Z_110 | 1 | 2 | 0.0021 | 0.1237 | 0 | 156.25 | 125
BLC_T2101 | BLC_I_Z_220 | BLC_I_Z_110 | 1 | 2 | 0.001 | 0.0646 | 0 | 312.5 | 250
BVK_T2101 | BVK_I_Z_220 | BVK_I_Z_110 | 1 | 2 | 0.001 | 0.064 | 0 | 312.5 | 250
BVK_T2102 | BVK_I_Z_220 | BVK_I_Z_110 | 1 | 2 | 0.001 | 0.064 | 0 | 312.5 | 250
BYH_T2101 | BYH_I_Z_220 | BYH_I_Z_110 | 1 | 2 | 0.001 | 0.064 | 0 | 312.5 | 250
BYH_T2102 | BYH_I_Z_220 | BYH_I_Z_110 | 1 | 2 | 0.001 | 0.064 | 0 | 312.5 | 250
CBT_T2101 | CBT_I_Z_220 | CBT_I_Z_110 | 1 | 2 | 0.001 | 0.0646 | 0 | 312.5 | 250
CBT_T2102 | CBT_I_Z_220 | CBT_I_Z_110 | 1 | 2 | 0.001 | 0.0646 | 0 | 312.5 | 250
CBT_T2103 | CBT_I_Z_220 | CBT_I_Z_110 | 1 | 2 | 0.001 | 0.0646 | 0 | 312.5 | 250
CBT_T2104 | CBT_I_Z_220 | CBT_I_Z_110 | 1 | 2 | 0.001 | 0.0646 | 0 | 312.5 | 250
CDU_T2101 | CDU_I_Z_220 | CDU_I_Z_110 | 1 | 2 | 0.00093 | 0.06152 | 0 | 312.5 | 250
CDU_T2102 | CDU_I_Z_220 | CDU_I_Z_110 | 1 | 2 | 0.00066 | 0.061 | 0 | 312.5 | 250
CKM_PST2201 | CKM_I_Z_220 | CKM_I_Z_220 | 1 | 0 | 0 | 0.029 | 0 | 437.5 | 350
CKM_T2101 | CKM_I_Z_220 | CKM_I_Z_110 | 1 | 2 | 0.001 | 0.0646 | 0 | 312.5 | 250
CKM_T2102 | CKM_I_Z_220 | CKM_I_Z_110 | 1 | 2 | 0.001 | 0.0646 | 0 | 312.5 | 250
CKM_T2103 | CKM_I_Z_220 | CKM_I_Z_110 | 1 | 2 | 0.001 | 0.0646 | 0 | 312.5 | 250
CKM_T2104 | CKM_I_Z_220 | CKM_I_Z_110 | 1 | 2 | 0.0004 | 0.0631 | 0 | 312.5 | 250
CLA_T2102 | CLA_I_Z_220 | CLA_I_Z_110 | 1 | 2 | 0.0013 | 0.0647 | 0 | 312.5 | 250
CSH_T2101 | CSH_I_Z_220 | CSH_I_Z_110 | 1 | 2 | 0.0004 | 0.0631 | 0 | 297.5 | 238
CSH_T2102 | CSH_I_Z_220 | CSH_I_Z_110 | 1 | 2 | 0.0004 | 0.0631 | 0 | 312.5 | 250
CSH_T2104 | CSH_I_Z_220 | CSH_I_Z_110 | 1 | 2 | 0.0021 | 0.1332 | 0 | 218.75 | 175
CNB_T4101 | CNB_I_Z_380 | CNB_I_Z_110 | 1 | 2 | 0.00048 | 0.072 | 0 | 625 | 500
CNB_T4102 | CNB_I_Z_380 | CNB_I_Z_110 | 1 | 2 | 0.00048 | 0.072 | 0 | 625 | 500
CUL_T2101 | CUL_I_Z_220 | CUL_I_Z_110 | 1 | 2 | 0.0005 | 0.064 | 0 | 312.5 | 250
DSN_T4201 | DSN_I_Z_380 | DSN_I_Z_220 | 1 | 2 | 0.0002 | 0.0317 | 0 | 625 | 500
DSN_T4202 | DSN_I_Z_380 | DSN_I_Z_220 | 1 | 2 | 0.0003 | 0.027 | 0 | 625 | 500
FIN_T2101 | FIN_I_Z_220 | FIN_I_Z_110 | 1 | 2 | 0.0013 | 0.0651 | 0 | 312.5 | 250
FIN_T2102 | FIN_I_Z_220 | FIN_I_Z_110 | 1 | 2 | 0.0013 | 0.0648 | 0 | 312.5 | 250
FIN_T2103 | FIN_I_Z_220 | FIN_I_Z_110 | 1 | 2 | 0.001 | 0.064 | 0 | 312.5 | 250
FIN_T2104 | FIN_I_Z_220 | FIN_I_Z_110 | 1 | 2 | 0.001 | 0.0638 | 0 | 312.5 | 250
FIN_T2105 | FIN_I_Z_220 | FIN_I_Z_110 | 1 | 2 | 0.001 | 0.064 | 0 | 312.5 | 250
FLA_T2101 | FLA_I_Z_220 | FLA_I_Z_110 | 1 | 2 | 0.0027 | 0.128 | 0 | 156.25 | 125
FLA_T2102 | FLA_I_Z_220 | FLA_I_Z_110 | 1 | 2 | 0.0008 | 0.1331 | 0 | 156.25 | 125
GI_T2101 | GI_I_Z_220 | GI_I_Z_110 | 1 | 2 | 0.0026 | 0.1331 | 0 | 156.25 | 125
GI_T2102 | GI_I_Z_220 | GI_I_Z_110 | 1 | 2 | 0.0023 | 0.1237 | 0 | 156.25 | 125
GOR_T2101 | GOR_I_Z_220 | GOR_I_Z_110 | 1 | 2 | 0.001 | 0.064 | 0 | 312.5 | 250
INC_T2102 | INC_I_Z_220 | INC_I_Z_110 | 1 | 2 | 0.001 | 0.0564 | 0 | 312.5 | 250
INC_T2104 | INC_I_Z_220 | INC_I_Z_110 | 1 | 2 | 0.0001 | 0.06 | 0 | 312.5 | 250
INC_T2101 | INC_I_Z_220 | INC_I_Z_110 | 1 | 2 | 0.001 | 0.0564 | 0 | 312.5 | 250
INC_T2103 | INC_I_Z_220 | INC_I_Z_110 | 1 | 2 | 0.0001 | 0.06 | 0 | 312.5 | 250
KLN_T2101 | KLN_I_Z_220 | KLN_I_Z_110 | 1 | 2 | 0.0065 | 0.2453 | 0 | 78.75 | 63
KLN_T2102 | KLN_I_Z_220 | KLN_I_Z_110 | 1 | 2 | 0.0095 | 0.2473 | 0 | 78.75 | 63
KLN_T2103 | KLN_I_Z_220 | KLN_I_Z_110 | 1 | 2 | 0.0004 | 0.0631 | 0 | 312.5 | 250
KLN_T2104 | KLN_I_Z_220 | KLN_I_Z_110 | 1 | 2 | 0.001 | 0.123 | 0 | 156.25 | 125
KLP_T2101 | KLP_I_Z_220 | KLP_I_Z_110 | 1 | 2 | 0.0004 | 0.0631 | 0 | 312.5 | 250
KLP_T2102 | KLP_I_Z_220 | KLP_I_Z_110 | 1 | 2 | 0.0004 | 0.0631 | 0 | 312.5 | 250
KLS_T2101 | KLS_I_Z_220 | KLS_I_Z_110 | 1 | 2 | 0.00132 | 0.1237 | 0 | 156.25 | 125
KLS_T2102 | KLS_I_Z_220 | KLS_I_Z_110 | 1 | 2 | 0.0008 | 0.1237 | 0 | 156.25 | 125
KNR_T2101 | KNR_I_Z_220 | KNR_I_Z_110 | 1 | 2 | 0.001 | 0.064 | 0 | 312.5 | 250
KNR_T2102 | KNR_I_Z_220 | KNR_I_Z_110 | 1 | 2 | 0.001 | 0.064 | 0 | 312.5 | 250
BLC_BELCAMP | BLC_I_Z_220 | BLC_I_Z_110 | 1 | 2 | 0.001 | 0.0646 | 0 | 312.5 | 250
CLA_T2101 | CLA_I_Z_220 | CLA_I_Z_110 | 1 | 2 | 0.0013 | 0.0647 | 0 | 312.5 | 250
KRA_T2101 | KRA_I_Z_220 | KRA_I_Z_110 | 1 | 2 | 0.0013 | 0.0647 | 0 | 312.5 | 250
KRA_T2102 | KRA_I_Z_220 | KRA_I_Z_110 | 1 | 2 | 0.0013 | 0.0652 | 0 | 312.5 | 250
LWD_T2101 | LWD_I_Z_220 | LWD_I_Z_110 | 1 | 2 | 0.001 | 0.064 | 0 | 312.5 | 250
LOU_T2101 | LOU_I_Z_220 | LOU_I_Z_110 | 1 | 2 | 0.0022 | 0.1331 | 0 | 156.25 | 125
LOU_T2103 | LOU_I_Z_220 | LOU_I_Z_110 | 1 | 2 | 0.0023 | 0.1324 | 0 | 156.25 | 125
LOU_T2102 | LOU_I_Z_220 | LOU_I_Z_110 | 1 | 2 | 0.0022 | 0.1324 | 0 | 156.25 | 125
LOU_T2104 | LOU_I_Z_220 | LOU_I_Z_110 | 1 | 2 | 0.001 | 0.064 | 0 | 312.5 | 250
LOU_AT1 | LOU_I_Z_220 | LOU_I_Z_275 | 1 | 2 | 0.0008 | 0.03 | 0 | 375 | 300
LOU_AT2 | LOU_I_Z_220 | LOU_I_Z_275 | 1 | 2 | 0.0008 | 0.015 | 0 | 750 | 600
LOU_AT3 | LOU_I_Z_275 | LOU_I_Z_220 | 1 | 2 | 0.0008 | 0.0303 | 0 | 375 | 300
MAY_T2101 | MAY_I_Z_220 | MAY_I_Z_110 | 1 | 2 | 0.0021 | 0.1339 | 0 | 156.25 | 125
MAY_T2102 | MAY_I_Z_220 | MAY_I_Z_110 | 1 | 2 | 0.001 | 0.064 | 0 | 297.5 | 238
MAY_T2103 | MAY_I_Z_220 | MAY_I_Z_110 | 1 | 2 | 0.0021 | 0.1324 | 0 | 156.25 | 125
MAY_T2104 | MAY_I_Z_220 | MAY_I_Z_110 | 1 | 2 | 0.001 | 0.064 | 0 | 312.5 | 250
MP_T4202_01 | MP_I_Z_380 | MP_I_Z_220 | 1 | 2 | 0.0003 | 0.027 | 0 | 625 | 500
MP_T2101 | MP_I_Z_220 | MP_I_Z_110 | 1 | 2 | 0.001 | 0.064 | 0 | 312.5 | 250
MP_T4202_2 | MP_I_Z_380 | MP_I_Z_220 | 1 | 2 | 0.0002 | 0.0329 | 0 | 625 | 500
OST_T4202 | OST_I_Z_380 | OST_I_Z_220 | 1 | 2 | 0.0003 | 0.027 | 0 | 625 | 500
PB_T2103 | PB_I_Z_220 | PB_I_Z_110 | 1 | 2 | 0.0013 | 0.059 | 0 | 312.5 | 250
PB_T2104 | PB_I_Z_220 | PB_I_Z_110 | 1 | 2 | 0.0013 | 0.0609 | 0 | 312.5 | 250
RAF_T2101 | RAF_I_Z_220 | RAF_I_Z_110 | 1 | 2 | 0.001 | 0.064 | 0 | 297.5 | 238
RAF_T2102 | RAF_I_Z_220 | RAF_I_Z_110 | 1 | 2 | 0.000446 | 0.0558 | 0 | 312.5 | 250
SH_T2102 | SH_I_Z_220 | SH_I_Z_110 | 1 | 2 | 0.00131 | 0.1237 | 0 | 156.25 | 125
SH_T2101 | SH_I_Z_220 | SH_I_Z_110 | 1 | 2 | 0.00574 | 0.1237 | 0 | 156.25 | 125
SRA_T2102 | SRA_I_Z_220 | SRA_I_Z_110 | 1 | 2 | 0.001 | 0.064 | 0 | 312.5 | 250
TB_T2101 | TB_I_Z_220 | TB_I_Z_110 | 1 | 2 | 0.00099 | 0.0554 | 0 | 297.5 | 238
TB_T2102 | TB_I_Z_220 | TB_I_Z_110 | 1 | 2 | 0.00099 | 0.0554 | 0 | 297.5 | 238
WOO_T4201 | WOO_I_Z_380 | WOO_I_Z_220 | 1 | 2 | 0.0002 | 0.0316 | 0 | 625 | 500
WOO_T4202 | WOO_I_Z_380 | WOO_I_Z_220 | 1 | 2 | 0.0002 | 0.0316 | 0 | 625 | 500
WOO_T4204 | WOO_I_Z_380 | WOO_I_Z_220 | 1 | 2 | 0.0002 | 0.027 | 0 | 687.5 | 550
WOO_WOODLAND | WOO_I_Z_380 | WOO_I_Z_260 | 1 | 2 | 0 | 0.024 | 0 | 727.5 | 582
AGH_1 | AGH_N_Z_110 | AGH_N_Z_33 | 1 | 2 | 0.00351 | 0.22176 | 0 | 112.5 | 90
AIR_1 | AIR_N_Z_110 | AIR_N_Z_33 | 1 | 2 | 0.0073 | 0.25 | 0 | 75 | 60
AIR_2 | AIR_N_Z_110 | AIR_N_Z_33 | 1 | 2 | 0.0073 | 0.25 | 0 | 75 | 60
ANT_1 | ANT_N_Z_110 | ANT_N_Z_33 | 1 | 2 | 0.00351 | 0.22176 | 0 | 112.5 | 90
ANT_2 | ANT_N_Z_110 | ANT_N_Z_33 | 1 | 2 | 0.00351 | 0.22257 | 0 | 112.5 | 90
MKL_1 | MKL_N_Z_110 | MKL_N_Z_33 | 1 | 2 | 0.00351 | 0.22518 | 0 | 112.5 | 90
MKL_2 | MKL_N_Z_110 | MKL_N_Z_33 | 1 | 2 | 0.00351 | 0.22518 | 0 | 112.5 | 90
BMA_1 | BMA_N_Z_110 | BMA_N_Z_33 | 1 | 2 | 0.00351 | 0.22023 | 0 | 112.5 | 90
BMA_2 | BMA_N_Z_110 | BMA_N_Z_33 | 1 | 2 | 0.00351 | 0.22167 | 0 | 112.5 | 90
BMA_3 | BMA_N_Z_110 | BMA_N_Z_33 | 1 | 2 | 0.00585 | 0.26037 | 0 | 112.5 | 90
BMA_4 | BMA_N_Z_110 | BMA_N_Z_33 | 1 | 2 | 0.00585 | 0.25803 | 0 | 112.5 | 90
BAN_1 | BAN_N_Z_110 | BAN_N_Z_33 | 1 | 2 | 0.00513 | 0.12399 | 0 | 37.5 | 30
BAN_2 | BAN_N_Z_110 | BAN_N_Z_33 | 1 | 2 | 0.0057 | 0.1242 | 0 | 37.5 | 30
BAN_3 | BAN_N_Z_110 | BAN_N_Z_33 | 1 | 2 | 0.0057 | 0.12501 | 0 | 37.5 | 30
BAN_4 | BAN_N_Z_110 | BAN_N_Z_33 | 1 | 2 | 0.0057 | 0.1245 | 0 | 37.5 | 30
BNH_1 | BNH_N_Z_110 | BNH_N_Z_33 | 1 | 2 | 0.00333 | 0.21771 | 0 | 112.5 | 90
BNH_2 | BNH_N_Z_110 | BNH_N_Z_33 | 1 | 2 | 0.00342 | 0.21717 | 0 | 112.5 | 90
BNM_1 | BNM_N_Z_110 | BNM_N_Z_33 | 1 | 2 | 0.00351 | 0.22149 | 0 | 112.5 | 90
BNM_2 | BNM_N_Z_110 | BNM_N_Z_33 | 1 | 2 | 0.00351 | 0.22149 | 0 | 112.5 | 90
BRO | BRO_N_Z_110 | BRO_N_Z_33 | 1 | 2 | 0.0035 | 0.16 | 0 | 125 | 100
CAR_1 | CAR_N_Z_110 | CAR_N_Z_33 | 1 | 2 | 0.00351 | 0.2232 | 0 | 112.5 | 90
CAR_2 | CAR_N_Z_110 | CAR_N_Z_33 | 1 | 2 | 0.00351 | 0.2232 | 0 | 112.5 | 90
CEN_1 | CEN_N_Z_110 | CEN_N_Z_33 | 1 | 2 | 0.00333 | 0.21798 | 0 | 112.5 | 90
CEN_2 | CEN_N_Z_110 | CEN_N_Z_33 | 1 | 2 | 0.00342 | 0.21771 | 0 | 112.5 | 90
COL (N)_1 | COL_N_Z_110 | COL_N_Z_33 | 1 | 2 | 0.00444 | 0.15072 | 0 | 75 | 60
COL (N)_2 | COL_N_Z_110 | COL_N_Z_33 | 1 | 2 | 0.0045 | 0.15048 | 0 | 75 | 60
CPS_1_110/33 | CPS_N_Z_110 | CPS_N_Z_33 | 1 | 2 | 0.00783 | 0.23031 | 0 | 112.5 | 90
CPS_2_110/33 | CPS_N_Z_110 | CPS_N_Z_33 | 1 | 2 | 0.00783 | 0.23157 | 0 | 112.5 | 90
CRG_1 | CRG_N_Z_110 | CRG_N_Z_33 | 1 | 2 | 0.00444 | 0.1509 | 0 | 75 | 60
CRG_2 | CRG_N_Z_110 | CRG_N_Z_33 | 1 | 2 | 0.00444 | 0.15048 | 0 | 75 | 60
CRE_1 | CRE_N_Z_110 | CRE_N_Z_33 | 1 | 2 | 0.006825 | 0.14648 | 0 | 93.75 | 75
CRE_2 | CRE_N_Z_110 | CRE_N_Z_33 | 1 | 2 | 0.006825 | 0.14753 | 0 | 93.75 | 75
DON_1 | DON_N_Z_110 | DON_N_Z_33 | 1 | 2 | 0.00714 | 0.21642 | 0 | 75 | 60
DON_2 | DON_N_Z_110 | DON_N_Z_33 | 1 | 2 | 0.00714 | 0.21948 | 0 | 75 | 60
DON_3 | DON_N_Z_110 | DON_N_Z_33 | 1 | 2 | 0.0036 | 0.21627 | 0 | 112.5 | 90
DON_4 | DON_N_Z_110 | DON_N_Z_33 | 1 | 2 | 0.00714 | 0.21948 | 0 | 75 | 60
DRU (N)_1 | DRU_N_Z_110 | DRU_N_Z_33 | 1 | 2 | 0.00549 | 0.21807 | 0 | 112.5 | 90
DRU (N)_2 | DRU_N_Z_110 | DRU_N_Z_33 | 1 | 2 | 0.00549 | 0.21834 | 0 | 112.5 | 90
CRR | CRR_N_Z_110 | CRR_N_Z_33 | 1 | 2 | 0.00351 | 0.22149 | 0 | 112.5 | 90
DUN_1 | DUN_N_Z_110 | DUN_N_Z_33 | 1 | 2 | 0.00783 | 0.23094 | 0 | 112.5 | 90
DUN_2 | DUN_N_Z_110 | DUN_N_Z_33 | 1 | 2 | 0.00783 | 0.23391 | 0 | 112.5 | 90
EDE_1 | EDE_N_Z_110 | EDE_N_Z_33 | 1 | 2 | 0.005625 | 0.12298 | 0 | 56.25 | 45
EDE_2 | EDE_N_Z_110 | EDE_N_Z_33 | 1 | 2 | 0.005535 | 0.12321 | 0 | 56.25 | 45
ENN (N)_1 | ENN_N_Z_110 | ENN_N_Z_33 | 1 | 2 | 0.00567 | 0.1224 | 0 | 56.25 | 45
ENN (N)_2 | ENN_N_Z_110 | ENN_N_Z_33 | 1 | 2 | 0.00567 | 0.12298 | 0 | 56.25 | 45
ENN (N)_3 | ENN_N_Z_110 | ENN_N_Z_33 | 1 | 2 | 0.00468 | 0.15072 | 0 | 75 | 60
FIN (N)_1 | FIN_N_Z_110 | FIN_N_Z_33 | 1 | 2 | 0.00342 | 0.11399 | 0 | 56.25 | 45
FIN (N)_2 | FIN_N_Z_110 | FIN_N_Z_33 | 1 | 2 | 0.00342 | 0.11471 | 0 | 56.25 | 45
GLE (N) | GLE_N_Z_110 | GLE_N_Z_33 | 1 | 2 | 0.00714 | 0.16152 | 0 | 75 | 60
GOR (N) | GOR_N_Z_110 | GOR_N_Z_33 | 1 | 2 | 0.00351 | 0.22149 | 0 | 112.5 | 90
KMT | KMT_N_Z_110 | KMT_N_Z_33 | 1 | 2 | 0.00351 | 0.22149 | 0 | 112.5 | 90
KNO_1 | KNO_N_Z_110 | KNO_N_Z_33 | 1 | 2 | 0.00351 | 0.22149 | 0 | 112.5 | 90
KNO_2 | KNO_N_Z_110 | KNO_N_Z_33 | 1 | 2 | 0.00351 | 0.22149 | 0 | 112.5 | 90
LAR_1 | LAR_N_Z_110 | LAR_N_Z_33 | 1 | 2 | 0.00522 | 0.12501 | 0 | 56.25 | 45
LAR_2 | LAR_N_Z_110 | LAR_N_Z_33 | 1 | 2 | 0.00522 | 0.1247 | 0 | 56.25 | 45
LIM (N)_1 | LIM_N_Z_110 | LIM_N_Z_33 | 1 | 2 | 0.005625 | 0.1264 | 0 | 56.25 | 45
LIM (N)_2 | LIM_N_Z_110 | LIM_N_Z_33 | 1 | 2 | 0.00549 | 0.12438 | 0 | 56.25 | 45
LIS (N)_1 | LIS_N_Z_110 | LIS_N_Z_33 | 1 | 2 | 0.00783 | 0.2286 | 0 | 112.5 | 90
LIS (N)_2 | LIS_N_Z_110 | LIS_N_Z_33 | 1 | 2 | 0.00774 | 0.23121 | 0 | 112.5 | 90
LMR_1 | LMR_N_Z_110 | LMR_N_Z_33 | 1 | 2 | 0.00342 | 0.1143 | 0 | 56.25 | 45
LMR_2 | LMR_N_Z_110 | LMR_N_Z_33 | 1 | 2 | 0.00342 | 0.11399 | 0 | 56.25 | 45
LOG_1 | LOG_N_Z_110 | LOG_N_Z_33 | 1 | 2 | 0.00576 | 0.12321 | 0 | 56.25 | 45
LOG_2 | LOG_N_Z_110 | LOG_N_Z_33 | 1 | 2 | 0.00576 | 0.126 | 0 | 56.25 | 45
NAR_1 | NAR_N_Z_110 | NAR_N_Z_33 | 1 | 2 | 0.0045 | 0.1503 | 0 | 75 | 60
NAR_2 | NAR_N_Z_110 | NAR_N_Z_33 | 1 | 2 | 0.00438 | 0.15 | 0 | 75 | 60
NEW (N)_1 | NEW_N_Z_110 | NEW_N_Z_33 | 1 | 2 | 0.00342 | 0.21843 | 0 | 112.5 | 90
NEW (N)_2 | NEW_N_Z_110 | NEW_N_Z_33 | 1 | 2 | 0.00342 | 0.21771 | 0 | 112.5 | 90
OMA_1 | OMA_N_Z_110 | OMA_N_Z_33 | 1 | 2 | 0.00351 | 0.22329 | 0 | 112.5 | 90
OMA_2 | OMA_N_Z_110 | OMA_N_Z_33 | 1 | 2 | 0.00351 | 0.2241 | 0 | 112.5 | 90
RSK | RSK_N_Z_110 | RSK_N_Z_33 | 1 | 2 | 0.00351 | 0.22149 | 0 | 112.5 | 90
RAT (N)_1 | RAT_N_Z_110 | RAT_N_Z_33 | 1 | 2 | 0.00783 | 0.22941 | 0 | 112.5 | 90
RAT (N)_2 | RAT_N_Z_110 | RAT_N_Z_33 | 1 | 2 | 0.00414 | 0.21618 | 0 | 112.5 | 90
ROS_1 | ROS_N_Z_110 | ROS_N_Z_33 | 1 | 2 | 0.00783 | 0.23184 | 0 | 112.5 | 90
ROS_2 | ROS_N_Z_110 | ROS_N_Z_33 | 1 | 2 | 0.00783 | 0.22797 | 0 | 112.5 | 90
SPR_1 | SPR_N_Z_110 | SPR_N_Z_33 | 1 | 2 | 0.00351 | 0.2223 | 0 | 112.5 | 90
SPR_2 | SPR_N_Z_110 | SPR_N_Z_33 | 1 | 2 | 0.00351 | 0.22239 | 0 | 112.5 | 90
STR (N)_1 | STR_N_Z_110 | STR_N_Z_33 | 1 | 2 | 0.00342 | 0.11349 | 0 | 56.25 | 45
STR (N)_2 | STR_N_Z_110 | STR_N_Z_33 | 1 | 2 | 0.00342 | 0.11322 | 0 | 56.25 | 45
TRE | TRE_N_Z_110 | TRE_N_Z_33 | 1 | 2 | 0.00351 | 0.22149 | 0 | 112.5 | 90
TMN | TMN_N_Z_110 | TMN_N_Z_33 | 1 | 2 | 0.0159 | 0.18456 | 0 | 75 | 60
WAR_1 | WAR_N_Z_110 | WAR_N_Z_33 | 1 | 2 | 0.00351 | 0.22329 | 0 | 112.5 | 90
WAR_2 | WAR_N_Z_110 | WAR_N_Z_33 | 1 | 2 | 0.00351 | 0.22392 | 0 | 112.5 | 90
BPS_1 | BPS_N_Z_275 | BPS_N_Z_110 | 1 | 2 | 0.0018 | 0.0641 | 0 | 300 | 240
BPS_2 | BPS_N_Z_275 | BPS_N_Z_110 | 1 | 2 | 0.0018 | 0.0641 | 0 | 300 | 240
CAS_1 | CAS_N_Z_275 | CAS_N_Z_110 | 1 | 2 | 0.0014 | 0.0639 | 0 | 300 | 240
CAS_2 | CAS_N_Z_275 | CAS_N_Z_110 | 1 | 2 | 0.0018 | 0.0641 | 0 | 300 | 240
CAS_3 | CAS_N_Z_275 | CAS_N_Z_110 | 1 | 2 | 0.0018 | 0.0656 | 0 | 300 | 240
CPS_1 | CPS_N_Z_275 | CPS_N_Z_110 | 1 | 2 | 0.001 | 0.0699 | 0 | 300 | 240
CPS_2 | CPS_N_Z_275 | CPS_N_Z_110 | 1 | 2 | 0.0014 | 0.0639 | 0 | 300 | 240
HAN_1 | HAN_N_Z_275 | HAN_N_Z_110 | 1 | 2 | 0.0018 | 0.0591 | 0 | 300 | 240
HAN_2 | HAN_N_Z_275 | HAN_N_Z_110 | 1 | 2 | 0.0018 | 0.0591 | 0 | 300 | 240
HAN_3 | HAN_N_Z_275 | HAN_N_Z_110 | 1 | 2 | 0.001 | 0.07 | 0 | 300 | 240
KEL_1 | KEL_N_Z_275 | KEL_N_Z_110 | 1 | 2 | 0.0018 | 0.0609 | 0 | 300 | 240
KEL_2 | KEL_N_Z_275 | KEL_N_Z_110 | 1 | 2 | 0.0018 | 0.0607 | 0 | 300 | 240
TAN_1 | TAN_N_Z_275 | TAN_N_Z_110 | 1 | 2 | 0.0018 | 0.0641 | 0 | 300 | 240
TAN_2 | TAN_N_Z_275 | TAN_N_Z_110 | 1 | 2 | 0.0018 | 0.0641 | 0 | 300 | 240
TAN_3 | TAN_N_Z_275 | TAN_N_Z_110 | 1 | 2 | 0.001 | 0.0698 | 0 | 300 | 240
TMN_1 | TMN_N_Z_275 | TMN_N_Z_110 | 1 | 2 | 0.0014 | 0.0644 | 0 | 300 | 240
TMN_2 | TMN_N_Z_275 | TMN_N_Z_110 | 1 | 2 | 0.0014 | 0.0644 | 0 | 300 | 240
Note on I1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Unvalidated assumption of 125% of continuous rating.
Note on F169: Richard Nayer: Winding 1-2

## ts_TLmax
timestep | AD_T2101 | ARK_T2101 | ARK_T2102 | BLC_T2101 | BVK_T2101 | BVK_T2102 | BYH_T2101 | BYH_T2102 | CBT_T2101 | CBT_T2102 | CBT_T2103 | CBT_T2104 | CDU_T2101 | CDU_T2102 | CKM_T2101 | CKM_T2102 | CKM_T2103 | CKM_T2104 | CLA_T2102 | CSH_T2101 | CSH_T2102 | CSH_T2104 | CNB_T4101 | CNB_T4102 | CUL_T2101 | DSN_T4201 | DSN_T4202 | FIN_T2101 | FIN_T2102 | FIN_T2103 | FIN_T2104 | FIN_T2105 | FLA_T2101 | FLA_T2102 | GI_T2101 | GI_T2102 | GOR_T2101 | INC_T2102 | INC_T2104 | INC_T2101 | INC_T2103 | KLN_T2101 | KLN_T2102 | KLN_T2103 | KLN_T2104 | KLP_T2101 | KLP_T2102 | KLS_T2101 | KLS_T2102 | KNR_T2101 | KNR_T2102 | BLC_BELCAMP | CLA_T2101 | KRA_T2101 | KRA_T2102 | LWD_T2101 | LOU_T2101 | LOU_T2103 | LOU_T2102 | LOU_T2104 | LOU_AT1 | LOU_AT2 | LOU_AT3 | MAY_T2101 | MAY_T2102 | MAY_T2103 | MAY_T2104 | MP_T4202_01 | MP_T2101 | MP_T4202_2 | OST_T4202 | PB_T2103 | PB_T2104 | RAF_T2101 | RAF_T2102 | SH_T2102 | SH_T2101 | SRA_T2102 | TB_T2101 | TB_T2102 | WOO_T4201 | WOO_T4202 | WOO_T4204 | WOO_WOODLAND | AGH_1 | AIR_1 | AIR_2 | ANT_1 | ANT_2 | MKL_1 | MKL_2 | BMA_1 | BMA_2 | BMA_3 | BMA_4 | BAN_1 | BAN_2 | BAN_3 | BAN_4 | BNH_1 | BNH_2 | BNM_1 | BNM_2 | BRO | CAR_1 | CAR_2 | CEN_1 | CEN_2 | COL (N)_1 | COL (N)_2 | CPS_1_110/33 | CPS_2_110/33 | CRG_1 | CRG_2 | CRE_1 | CRE_2 | DON_1 | DON_2 | DON_3 | DON_4 | DRU (N)_1 | DRU (N)_2 | CRR | DUN_1 | DUN_2 | EDE_1 | EDE_2 | ENN (N)_1 | ENN (N)_2 | ENN (N)_3 | FIN (N)_1 | FIN (N)_2 | GLE (N) | GOR (N) | KMT | KNO_1 | KNO_2 | LAR_1 | LAR_2 | LIM (N)_1 | LIM (N)_2 | LIS (N)_1 | LIS (N)_2 | LMR_1 | LMR_2 | LOG_1 | LOG_2 | NAR_1 | NAR_2 | NEW (N)_1 | NEW (N)_2 | OMA_1 | OMA_2 | RSK | RAT (N)_1 | RAT (N)_2 | ROS_1 | ROS_2 | SPR_1 | SPR_2 | STR (N)_1 | STR (N)_2 | TRE | TMN | WAR_1 | WAR_2 | BPS_1 | BPS_2 | CAS_1 | CAS_2 | CAS_3 | CPS_1 | CPS_2 | HAN_1 | HAN_2 | HAN_3 | KEL_1 | KEL_2 | TAN_1
t-1 | 125 | 63 | 125 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 238 | 250 | 175 | 500 | 500 | 250 | 500 | 500 | 250 | 250 | 250 | 250 | 250 | 125 | 125 | 125 | 125 | 250 | 250 | 250 | 250 | 250 | 63 | 63 | 250 | 125 | 250 | 250 | 125 | 125 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 125 | 125 | 125 | 250 | 300 | 600 | 300 | 125 | 238 | 125 | 250 | 500 | 250 | 500 | 500 | 250 | 250 | 238 | 250 | 125 | 125 | 250 | 238 | 238 | 500 | 500 | 550 | 582 | 90 | 60 | 60 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 30 | 30 | 30 | 30 | 90 | 90 | 90 | 90 | 100 | 90 | 90 | 90 | 90 | 60 | 60 | 90 | 90 | 60 | 60 | 75 | 75 | 60 | 60 | 90 | 60 | 90 | 90 | 90 | 90 | 90 | 45 | 45 | 45 | 45 | 60 | 45 | 45 | 60 | 90 | 90 | 90 | 90 | 45 | 45 | 45 | 45 | 90 | 90 | 45 | 45 | 45 | 45 | 60 | 60 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 45 | 45 | 90 | 60 | 90 | 90 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240

## generator
busname | name | Market ID | description | export_policy | lifo_group | lifo_position | prorata_groups | MUON_group | stat | PGLB | PGUB | FuelType | synchronous | costc1 | costc0 | bid | offer
WOO_I_Z_380 | EWIC | EWIC | EWIC | Pro-Rata |  |  | ROI/1 |  | 1 | -504 | 526 | interconnector | No | 70 | 0 | 10000 | 0
GLE_I_Z_110 | DV1 | GU_401240 | Dromdeeveen Windfarm | Pro-Rata |  |  | ROI-W/2,ROI-SW/3a,ROI-SW/3b,ROI-SW/3c,ROI/1,ROI/1 |  | 1 | 0 | 27 | wind | No | 0 | 0 | 9000 | 0
LWN_I_Z_220 | GLK | I_ROIGRLK | Greenlink | Pro-Rata |  |  | ROI/1 |  | 0 | -500 | 500 | interconnector | No | 70 | 0 | 10000 | 0
SLB_I_Z_110 | SB1 | GU_401900 | Sliabh Bawn Windfarm | Pro-Rata |  |  | ROI-NW/4,ROI-W/1,ROI-W/2,ROI/1 |  | 1 | 0 | 58 | wind | No | 0 | 0 | 9000 | 0
SLC_I_Z_110 | KD1 | GU_403940 | Knockalassa Windfarm | Pro-Rata |  |  | ROI-W/1,ROI-W/2,ROI/1 |  | 1 | 0 | 27 | wind | No | 0 | 0 | 9000 | 0
SLC_I_Z_110 | RD1 | GU_402270 | Boolinrudda Windfarm | Pro-Rata |  |  | ROI-W/1,ROI-W/2,ROI/1 |  | 1 | 0 | 45 | wind | No | 0 | 0 | 9000 | 0
SKY_I_Z_110 | OY1 | GU_403760 | Oweninny Wind Farm | Pro-Rata |  |  | ROI-NW/4,ROI-W/1,ROI-W/2,ROI-W/6,ROI-W/7,ROI-W/8,ROI/1 |  | 1 | 0 | 89 | wind | No | 0 | 0 | 9000 | 0
SKY_I_Z_110 | OY2 | GU_405130 | Oweninny 2 Windfarm | Pro-Rata |  |  | ROI-NW/4,ROI-W/1,ROI-W/2,ROI-W/6,ROI-W/7,ROI-W/8,ROI/1 |  | 1 | 0 | 83 | wind | No | 0 | 0 | 9000 | 0
TRI_I_Z_110 | KW1 | GU_404200 | Knockawarriga 1 Windfarm | Pro-Rata |  |  | ROI-W/2,ROI/1 |  | 1 | 0 | 22.5 | wind | No | 0 | 0 | 9000 | 0
TRI_I_Z_110 | TN2 | GU_400600 | Tournafulla Generatot Unit | Pro-Rata |  |  | ROI-W/2,ROI/1 |  | 1 | 0 | 17.2 | wind | No | 0 | 0 | 9000 | 0
AD_I_Z_220 | AT1 | GU_400181 | AGHADA CT11 Generator Unit | Individual |  |  | ROI/1 | S_REP_ROI,S_MWMAX_CRK_MW,S_MWMAX_STH_MW | 1 | 15 | 90 | multi_fuel | Yes | 109.44 | 12033.5 | 108.19 | 109.44
AD_I_Z_220 | AT2 | GU_400182 | AGHADA CT12 Generator Unit | Individual |  |  | ROI/1 | S_REP_ROI,S_MWMAX_CRK_MW,S_MWMAX_STH_MW | 1 | 15 | 90 | multi_fuel | Yes | 109.45 | 12033.5 | 108.18 | 109.45
AD_I_Z_220 | AT4 | GU_400183 | AGHADA CT14 Generator Unit | Individual |  |  | ROI/1 | S_REP_ROI,S_MWMAX_CRK_MW,S_MWMAX_STH_MW | 1 | 15 | 90 | multi_fuel | Yes | 109.46 | 12033.5 | 108.17 | 109.46
AD_I_Z_220 | AD2 | GU_400850 | Aghada 2 Generator Unit | Individual |  |  | ROI/1 | S_NBMIN_ROImin,S_MWMAX_CRK_MW,S_MWMAX_STH_MW | 1 | 120 | 449 | multi_fuel | Yes | 40.97 | 57991.36 | 40.96 | 40.97
AGH_N_Z_110 | MYM | GU_503860 | Molly Mountain Wind Farm | Pro-Rata |  |  | NI/2,NI/3,NI/4 |  | 1 | 0 | 15 | wind | No | 0 | 0 | 9000 | 0
AGH_N_Z_110 | SL2 | GU_503900 | Slieve Rushen Windfarm | Pro-Rata |  |  | NI/2,NI/3,NI/4 |  | 1 | 0 | 54 | wind | No | 0 | 0 | 9000 | 0
ANT_N_Z_110 | CBY | GU_501410 | Corby Knowe Windfarm | Pro-Rata |  |  | NI/4 |  | 1 | 0 | 5.4 | wind | No | 0 | 0 | 9000 | 0
AA_I_Z_110 | AA1 | GU_400200 | Ardnacrusha 1 Generator Unit | Individual |  |  | ROI-W/1,ROI-W/2,ROI/1 |  | 1 | 11.9 | 21 | hydro | Yes | 80 | 0 | 8000 | 80
AA_I_Z_110 | AA2 | GU_400201 | Ardnacrusha 2 Generator Unit | Individual |  |  | ROI-W/1,ROI-W/2,ROI/1 |  | 1 | 11.9 | 22 | hydro | Yes | 80 | 0 | 8000 | 80
AA_I_Z_110 | AA3 | GU_400202 | Ardnacrusha 3 Generator Unit | Individual |  |  | ROI-W/1,ROI-W/2,ROI/1 |  | 1 | 11.9 | 19 | hydro | Yes | 0 | 0 | 8000 | 0
AA_I_Z_110 | AA4 | GU_400203 | Ardnacrusha 4 Generator Unit | Individual |  |  | ROI-W/1,ROI-W/2,ROI/1 |  | 1 | 11.9 | 24 | hydro | Yes | 80 | 0 | 8000 | 80
ARK_I_Z_110 | ABK | GU_401020 | ESB Arklow Bank | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 25.6 | wind | No | 0 | 0 | 9000 | 0
ARK_I_Z_110 | RL1 | GU_401940 | Raheenleagh | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 35.2 | wind | No | 0 | 0 | 9000 | 0
ARK_I_Z_110 | YR1 | GU_404460 | Ballycumber Windfarm | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 18 | wind | No | 0 | 0 | 9000 | 0
ATE_I_Z_110 | AH1 | GU_401380 | Athea Wind Farm | Pro-Rata |  |  | ROI-W/2,ROI-W/2,ROI/1 |  | 1 | 0 | 34.35 | wind | No | 0 | 0 | 9000 | 0
ATE_I_Z_110 | XT1 | GU_404000 | Beenanaspuck and Tobertoreen Windfarm | Pro-Rata |  |  | ROI-W/2,ROI-W/2,ROI/1 |  | 1 | 0 | 24 | wind | No | 0 | 0 | 9000 | 0
AUG_I_Z_110 | SK3 | GU_400120 | Sealrock 3 Generator Unit | Individual |  |  | ROI/1 |  | 1 | 40 | 83 | multi_fuel | Yes | 74.29 | 12837 | -1000 | 74.29
AUG_I_Z_110 | SK4 | GU_400121 | Sealrock 4 Generator Unit | Individual |  |  | ROI/1 |  | 1 | 40 | 83 | multi_fuel | Yes | 74.29 | 12837 | -1000 | 74.29
BPS_N_Z_110 | BGT1 | GU_500283 | Ballylumford GT1 | Individual |  |  | NI/4 | S_MWMAX_NI_GT | 1 | 8 | 58 | distillate | Yes | 251.99 | 20696.55 | 246.74 | 251.99
BPS_N_Z_110 | BGT2 | GU_500284 | Ballylumford GT2 | Individual |  |  | NI/4 | S_MWMAX_NI_GT | 1 | 8 | 58 | distillate | Yes | 251.99 | 18208.86 | 246.74 | 251.99
BPS_N_Z_110 | B10 | GU_503740 | Ballylumford Generator Unit B10 | Individual |  |  | NI/4 | S_NBMIN_MINNIU | 1 | 63 | 101 | gas | Yes | 85.59 | 12758.51 | 79.19 | 85.59
BPS_N_Z_275 | B31 | GU_503720 | Ballylumford Generator Unit B31 | Individual |  |  | NI/4 | S_NBMIN_MINNIU | 1 | 113 | 247 | multi_fuel | Yes | 81.77 | 22451.27 | 75.91 | 81.77
BPS_N_Z_275 | B32 | GU_503730 | Ballylumford Generator Unit B32 | Individual |  |  | NI/4 | S_NBMIN_MINNIU | 1 | 113 | 247 | multi_fuel | Yes | 81.77 | 22451.27 | 75.91 | 81.77
BYC_N_Z_275 | M | MOYLE | Moyle | Pro-Rata |  |  | NI/4 |  | 1 | -441 | 410 | interconnector | No | 70 | 0 | 10000 | 0
BWR_I_Z_110 | BW1 | GU_405890 | Ballywater Windfarm | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 42 | wind | No | 0 | 0 | 9000 | 0
BAL_I_Z_110 | HS1 | GU_405090 | Hilltown Solar Farm | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 10 | solar | No | 0 | 0 | 9000 | 0
BMA_N_Z_110 | RHY | GU_501680 | Rathsherry Wind Farm | Pro-Rata |  |  | NI/4 |  | 1 | 0 | 21.15 | wind | No | 0 | 0 | 9000 | 0
BMA_N_Z_110 | EGH | GU_501720 | Elginny Hill Wind Farm | Pro-Rata |  |  | NI/4 |  | 1 | 0 | 23 | wind | No | 0 | 0 | 9000 | 0
BAN_N_Z_110 | BLD | GU_504250 | Ballydown Battery | Individual |  |  | NI/4 |  | 0 | 0 | 12.224 | multi_fuel | Yes | 500 | 0 | 0 | 500
BAR_I_T_110 | BF1 | GU_401810 | Barranafaddock Windfarm | Pro-Rata |  |  | ROI-W/2,ROI/1 |  | 1 | 0 | 32.4 | wind | No | 0 | 0 | 9000 | 0
BK_I_Z_110 | SS1 | GU_406560 | Sheskin Windfarm | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 16.8 | wind | No | 0 | 0 | 9000 | 0
BIN_I_Z_110 | CU1 | GU_401190 | Clady Generating Station | Individual |  |  | ROI-NW/1,ROI-NW/3,ROI-NW/4,ROI-W/2,ROI/1 |  | 1 | 0 | 4.3 | hydro | Yes | 0 | 0 | 8000 | 0
BIN_I_Z_110 | MC1 | GU_405870 | Airoshin Generator Unit | Pro-Rata |  |  | ROI-NW/1,ROI-NW/3,ROI-NW/4,ROI-W/2,ROI/1 |  | 1 | 0 | 11.9 | wind | No | 0 | 0 | 9000 | 0
BIN_I_Z_110 | YV2 | GU_404630 | Clogheravaddy WF 2 | Pro-Rata |  |  | ROI-NW/1,ROI-NW/3,ROI-NW/4,ROI-W/2,ROI/1 |  | 1 | 0 | 10.8 | wind | No | 0 | 0 | 9000 | 0
BLU_I_Z_110 | NA1 | GU_406520 | Blundelstown Solar Farm | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 60 | solar | No | 0 | 0 | 9000 | 0
BGH_I_Z_110 | BG1 | GU_400910 | Boggeragh Windfarm Generator Unit | Pro-Rata |  |  | ROI-W/2,ROI/1 |  | 1 | 0 | 57 | wind | No | 0 | 0 | 9000 | 0
BGH_I_Z_110 | BG2 | GU_401840 | Boggeragh 2 Windfarm | Pro-Rata |  |  | ROI-W/2,ROI/1 |  | 1 | 0 | 65.7 | wind | No | 0 | 0 | 9000 | 0
BGH_I_Z_110 | ES1 | GU_404340 | Esk Windfarm | Pro-Rata |  |  | ROI-W/2,ROI/1 |  | 1 | 0 | 23.2 | wind | No | 0 | 0 | 9000 | 0
BGH_I_Z_110 | CD1 | GU_401070 | Carraigcannon Windfarm | Pro-Rata |  |  | ROI-W/2,ROI/1 |  | 1 | 0 | 20 | wind | No | 0 | 0 | 9000 | 0
BGN_I_Z_110 | QA1 | GU_407330 | Moanvane Windfarm | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 56.4 | wind | No | 0 | 0 | 9000 | 0
BOL_I_Z_110 | BT1 | GU_401720 | Booltiagh Windfarm | Pro-Rata |  |  | ROI-W/1,ROI-W/2,ROI/1 |  | 1 | 0 | 20 | wind | No | 0 | 0 | 9000 | 0
BOL_I_Z_110 | BT2 | GU_401730 | Booltiagh 2 Wind Farm | Pro-Rata |  |  | ROI-W/1,ROI-W/2,ROI/1 |  | 1 | 0 | 12 | wind | No | 0 | 0 | 9000 | 0
BOL_I_Z_110 | LY1 | GU_403950 | Lissycasey Windfarm | Pro-Rata |  |  | ROI-W/1,ROI-W/2,ROI/1 |  | 1 | 0 | 13.4 | wind | No | 0 | 0 | 9000 | 0
BOL_I_Z_110 | SF1 | GU_403800 | Sorrell Island 1 Windfarm | Pro-Rata |  |  | ROI-W/1,ROI-W/2,ROI/1 |  | 1 | 0 | 24 | wind | No | 0 | 0 | 9000 | 0
BOL_I_Z_110 | SF2 | GU_404480 | Sorrell Island 2 Windfarm | Pro-Rata |  |  | ROI-W/1,ROI-W/2,ROI/1 |  | 1 | 0 | 8.55 | wind | No | 0 | 0 | 9000 | 0
BOL_I_Z_110 | BJ1 | GU_403770 | Boolynagleragh Windfarm | Pro-Rata |  |  | ROI-W/1,ROI-W/2,ROI/1 |  | 1 | 0 | 36.98 | wind | No | 0 | 0 | 9000 | 0
BRO_N_Z_110 | BKY | GU_501670 | Brockaghboy | Pro-Rata |  |  | NI/1,NI/4,NI/5 |  | 1 | 0 | 47.5 | wind | No | 0 | 0 | 9000 | 0
CAH_I_Z_110 | YM1 | GU_406710 | Ballymacadam Solar Farm | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 21 | solar | No | 0 | 0 | 9000 | 0
CLW_I_Z_110 | GE1 | GU_401060 | Gortahile Windfarm Ltd Generator Unit | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 20 | wind | No | 0 | 0 | 9000 | 0
CAR_N_Z_110 | CNH | GU_501210 | Carn Hill Wind Farm | Pro-Rata |  |  | NI/4 |  | 1 | 0 | 13.8 | wind | No | 0 | 0 | 9000 | 0
CD_I_Z_110 | LE3 | GU_400290 | Carrigadrohid Generator Unit | Individual |  |  | ROI/1 |  | 1 | 3 | 8 | hydro | Yes | 80 | 0 | 8000 | 80
CDN_I_Z_110 | XA1 | GU_404330 | Carrigdangan Windfarm | Pro-Rata |  |  | ROI-W/2,ROI/1 |  | 1 | 0 | 54.3 | wind | No | 0 | 0 | 9000 | 0
CBR_I_Z_110 | MX1 | GU_403740 | Raheen Barr Wind Farm | Pro-Rata |  |  | ROI-NW/4,ROI-W/1,ROI-W/2,ROI-W/6,ROI/1 |  | 1 | 0 | 18.7 | wind | No | 0 | 0 | 9000 | 0
CF_I_Z_110 | AS1 | GU_401820 | Acres Windfarm | Pro-Rata |  |  | ROI-NW/3,ROI-NW/4,ROI-W/2,ROI/1 |  | 1 | 0 | 17.5 | wind | No | 0 | 0 | 9000 | 0
CF_I_Z_110 | ER3 | GU_400220 | Erne 3 Generator Unit | Individual |  |  | ROI-NW/3,ROI-NW/4,ROI-W/2,ROI/1 |  | 1 | 5 | 22.5 | hydro | Yes | 80 | 0 | 8000 | 80
CF_I_Z_110 | ER4 | GU_400221 | Erne 4 Generator Unit | Individual |  |  | ROI-NW/3,ROI-NW/4,ROI-W/2,ROI/1 |  | 1 | 5 | 22.5 | hydro | Yes | 80 | 0 | 8000 | 80
CTN_I_Z_110 | CP1 | GU_402150 | Cappawhite | Pro-Rata |  |  | ROI-W/1,ROI-W/2,ROI-W/4,ROI/1 |  | 1 | 0 | 52 | wind | No | 0 | 0 | 9000 | 0
CTN_I_Z_110 | CP3 | GU_402340 | Cappawhite B Windfarm | Pro-Rata |  |  | ROI-W/1,ROI-W/2,ROI-W/4,ROI/1 |  | 1 | 0 | 14.132 | wind | No | 0 | 0 | 9000 | 0
CTN_I_Z_110 | GM1 | GU_401740 | Garracummer Wind Farm Ltd | Pro-Rata |  |  | ROI-W/1,ROI-W/2,ROI-W/4,ROI/1 |  | 1 | 0 | 38 | wind | No | 0 | 0 | 9000 | 0
CTN_I_Z_110 | GU1 | GU_401250 | Glenough Windfarm | Pro-Rata |  |  | ROI-W/1,ROI-W/2,ROI-W/4,ROI/1 |  | 1 | 0 | 32.5 | wind | No | 0 | 0 | 9000 | 0
CTN_I_Z_110 | GY1 | GU_404470 | Glencarbry Windfarm | Pro-Rata |  |  | ROI-W/1,ROI-W/2,ROI-W/4,ROI/1 |  | 1 | 0 | 33 | wind | No | 0 | 0 | 9000 | 0
CHA_I_Z_110 | KQ1 | GU_403930 | Knocknatallig Windfarm | Pro-Rata |  |  | ROI-W/2,ROI-SW/3c,ROI/1 |  | 1 | 0 | 18.3 | wind | No | 0 | 0 | 9000 | 0
CHA_I_Z_110 | PO1 | GU_402190 | Castlepook Windfarm | Pro-Rata |  |  | ROI-W/2,ROI-SW/3c,ROI/1 |  | 1 | 0 | 33.1 | wind | No | 0 | 0 | 9000 | 0
CLH_I_Z_110 | CJ1 | GU_400660 | Pallas Generator Unit | Pro-Rata |  |  | ROI-W/2,ROI/1 |  | 1 | 0 | 37.85 | wind | No | 0 | 0 | 9000 | 0
CLH_I_Z_110 | CJ2 | GU_401980 | Clahane 2 Windfarm | Pro-Rata |  |  | ROI-W/2,ROI/1 |  | 1 | 0 | 14 | wind | No | 0 | 0 | 9000 | 0
CL_I_Z_110 | ER1 | GU_400210 | Erne 1 Generator Unit | Individual |  |  | ROI/1 |  | 1 | 4 | 10 | hydro | Yes | 80 | 0 | 8000 | 80
CL_I_Z_110 | ER2 | GU_400211 | Erne 2 Generator Unit | Individual |  |  | ROI/1 |  | 1 | 4 | 10 | hydro | Yes | 80 | 0 | 8000 | 80
CBL_I_Z_110 | CL1 | GU_404570 | Cloghboola Wind Farm | Pro-Rata |  |  | ROI-W/2 |  | 1 | 0 | 46 | wind | No | 0 | 0 | 9000 | 0
CBL_I_Z_110 | DA1 | GU_404490 | Glanaruddery 1 Windfarm | Pro-Rata |  |  | ROI-W/2 |  | 1 | 0 | 20 | wind | No | 0 | 0 | 9000 | 0
CBL_I_Z_110 | DA2 | GU_404500 | Glanaruddery 2 Windfarm | Pro-Rata |  |  | ROI-W/2 |  | 1 | 0 | 12 | wind | No | 0 | 0 | 9000 | 0
CBL_I_Z_110 | KI1 | GU_402280 | Cloghanaleskirt Windfarm | Pro-Rata |  |  | ROI-W/2 |  | 1 | 0 | 11.5 | wind | No | 0 | 0 | 9000 | 0
CLO_I_Z_110 | OA1 | GU_404930 | Croaghonagh Windfarm | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 90 | wind | No | 0 | 0 | 9000 | 0
CPS_N_Z_110 | GAR | GU_500720 | Garves Wind Farm | Pro-Rata |  |  | NI/1,NI/4 |  | 1 | 0 | 15 | wind | No | 0 | 0 | 9000 | 0
CPS_N_Z_110 | GRU | GU_504240 | Gruig Wind Farm | Pro-Rata |  |  | NI/1,NI/4 |  | 1 | 0 | 25 | wind | No | 0 | 0 | 9000 | 0
CPS_N_Z_110 | DMR | GU_501250 | Dunmore Wind Farm | Pro-Rata |  |  | NI/1,NI/4 |  | 1 | 0 | 21 | wind | No | 0 | 0 | 9000 | 0
CPS_N_Z_110 | DBG | GU_503920 | Dunbeg Wind Farm | Pro-Rata |  |  | NI/1,NI/4 |  | 1 | 0 | 42 | wind | No | 0 | 0 | 9000 | 0
CPS_N_Z_110 | LPS | GU_501350 | Lisahally Biomass Generator | Individual |  |  | NI/1,NI/4 |  | 1 | 12.74 | 17.6 | biomass | Yes | 21.76 | 47815.76 | 8000 | 21.76
CPS_N_Z_110 | MBY | GU_501360 | Monnaboy Wind Farm | Pro-Rata |  |  | NI/1,NI/4 |  | 1 | 0 | 12 | wind | No | 0 | 0 | 9000 | 0
CPS_N_Z_110 | CGT8 | GU_500040 | Coolkeeragh | Individual |  |  | NI/1,NI/4 | S_MWMAX_NI_GT | 1 | 211 | 425 | multi_fuel | Yes | 51.61 | 96443.23 | 51.59 | 51.61
CPS_N_Z_110 | C30 | GU_500041 | Coolkeeragh | Individual |  |  | NI/1,NI/4 | S_NBMIN_MINNIU,S_NBMIN_MINNI3,S_NBMIN_CPS | 1 | 8 | 53 | distillate | Yes | 206.04 | 17041.17 | 206.04 | 206.04
CGL_I_Z_110 | CG1 | GU_404210 | Coomagearlahy Generator Unit | Pro-Rata |  |  | ROI-W/2,ROI/1 |  | 1 | 0 | 42.5 | wind | No | 0 | 0 | 9000 | 0
CGL_I_Z_110 | CG2 | GU_400730 | SWS Green Energy Gen Unit (Sillahertane) | Pro-Rata |  |  | ROI-W/2,ROI/1 |  | 1 | 0 | 8.5 | wind | No | 0 | 0 | 9000 | 0
CGL_I_Z_110 | CG3 | GU_400731 | SWS Kilgarvan Ext Inchincoosh | Pro-Rata |  |  | ROI-W/2,ROI/1 |  | 1 | 0 | 30 | wind | No | 0 | 0 | 9000 | 0
CTG_I_Z_110 | YT1 | GU_403810 | Cleanrath | Pro-Rata |  |  | ROI-W/2,ROI/1 |  | 1 | 0 | 42.64 | wind | No | 0 | 0 | 9000 | 0
CTG_I_Z_110 | GD1 | GU_403790 | Grousemount Windfarm | Pro-Rata |  |  | ROI-W/2,ROI/1 |  | 1 | 0 | 114.2 | wind | No | 0 | 0 | 9000 | 0
CDL_I_Z_110 | DL1 | GU_402110 | Cordal 1 Windfarm | Pro-Rata |  |  | ROI-W/2,ROI/1 |  | 1 | 0 | 36 | wind | No | 0 | 0 | 9000 | 0
CDL_I_Z_110 | DL2 | GU_402130 | Cordal 2 Windfarm | Pro-Rata |  |  | ROI-W/2,ROI/1 |  | 1 | 0 | 54 | wind | No | 0 | 0 | 9000 | 0
CDL_I_Z_110 | OG1 | GU_403920 | Coollegrean Windfarm | Pro-Rata |  |  | ROI-W/2,ROI/1 |  | 1 | 0 | 17.5 | wind | No | 0 | 0 | 9000 | 0
CDL_I_Z_110 | ST1 | GU_402250 | Scartaglen 1 Windfarm | Pro-Rata |  |  | ROI-W/2,ROI/1 |  | 1 | 0 | 34.5 | wind | No | 0 | 0 | 9000 | 0
CDL_I_Z_110 | ST2 | GU_402260 | Scartaglen 2 Windfarm | Pro-Rata |  |  | ROI-W/2,ROI/1 |  | 1 | 0 | 4.8 | wind | No | 0 | 0 | 9000 | 0
CDY_I_Z_110 | TM2 | GU_402160 | Tullynamoyle Windfarm 2 | Pro-Rata |  |  | ROI-NW/3,ROI-NW/4,ROI-W/1,ROI-W/2,ROI/1 |  | 1 | 0 | 10.3 | wind | No | 0 | 0 | 9000 | 0
CDY_I_Z_110 | TM3 | GU_402200 | Tullynamoyle 3 Windfarm | Pro-Rata |  |  | ROI-NW/3,ROI-NW/4,ROI-W/1,ROI-W/2,ROI/1 |  | 1 | 0 | 13.58 | wind | No | 0 | 0 | 9000 | 0
CDU_I_Z_110 | FG2 | GU_403680 | Corduff_OCGT | Individual |  |  | ROI/1 | S_REP_ROI | 1 | 22.5 | 63.5 | multi_fuel | Yes | 112.87 | 5161.24 | 111.57 | 112.87
CUN_I_Z_110 | KG2 | GU_400021 | Dunneil Windfarm (Kingsmountain Phase 2) | Pro-Rata |  |  | ROI-NW/3,ROI-NW/4,ROI-W/1,ROI-W/2,ROI-W/6,ROI-W/8,ROI/1 |  | 1 | 0 | 11.05 | wind | No | 0 | 0 | 9000 | 0
CUN_I_Z_110 | KGM | GU_400020 | Kingsmountain Generator Unit | Pro-Rata |  |  | ROI-NW/3,ROI-NW/4,ROI-W/1,ROI-W/2,ROI-W/6,ROI-W/8,ROI/1 |  | 1 | 0 | 25 | wind | No | 0 | 0 | 9000 | 0
CUS_I_Z_110 | ED1 | GU_401860 | Edenderry Power Supply | Individual |  |  | ROI/1 |  | 1 | 41.15 | 118 | peat | Yes | 18.53 | 30753.26 | 7000 | 18.53
CUS_I_Z_110 | ED3 | GU_401010 | Cushaling Power | Individual |  |  | ROI/1 | S_REP_ROI | 1 | 20 | 58 | distillate | Yes | 506.96 | 925.19 | 506.96 | 506.96
CUS_I_Z_110 | ED5 | GU_401011 | Cushaling Power | Individual |  |  | ROI/1 | S_REP_ROI | 1 | 20 | 58 | distillate | Yes | 506.95 | 925.19 | 506.95 | 506.95
DLT_I_Z_110 | MM1 | GU_403400 | Magheramore Windfarm | Pro-Rata |  |  | ROI-NW/4,ROI-W/1,ROI-W/2,ROI-W/6,ROI/1 |  | 1 | 0 | 40.8 | wind | No | 0 | 0 | 9000 | 0
DEE_I_Z_110 | QB1 | GU_407030 | Gaskinstown Solar Farm | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 85 | solar | No | 0 | 0 | 9000 | 0
DYN_I_Z_110 | DY1 | GU_401440 | Derrybrien Wind Farm | Pro-Rata |  |  | ROI-W/1,ROI-W/2,ROI/1 |  | 1 | 0 | 59.5 | wind | No | 0 | 0 | 9000 | 0
DEY_I_Z_110 | LU1 | GU_407520 | Lumcloon ESS 1 | Individual |  |  | ROI/1 |  | 0 | 0 | 50 | multi_fuel | Yes | 1150 | 0 | 0 | 1150
DEY_I_Z_110 | LU2 | GU_407530 | Lumcloon ESS 2 | Individual |  |  | ROI/1 |  | 0 | 0 | 50 | multi_fuel | Yes | 1150 | 0 | 0 | 1150
DEY_I_Z_110 | NC1 | GU_405160 | Cloghan Wind Farm | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 34 | wind | No | 0 | 0 | 9000 | 0
DER_I_Z_110 | RP1 | GU_400770 | Rhode Peaking 1 Generator Unit | Individual |  |  | ROI/1 | S_REP_ROI | 1 | 5 | 52 | distillate | Yes | 207.38 | 839.54 | 190.97 | 207.38
DER_I_Z_110 | RP2 | GU_400771 | Rhode Peaking 2 Generator Unit | Individual |  |  | ROI/1 | S_REP_ROI | 1 | 5 | 52 | distillate | Yes | 207.38 | 839.54 | 190.97 | 207.38
DRO_I_Z_110 | DR1 | GU_400920 | Dromada Windfarm Generator Unit | Pro-Rata |  |  | ROI-W/2,ROI/1 |  | 1 | 0 | 28.5 | wind | No | 0 | 0 | 9000 | 0
DRQ_N_Z_110 | CNV | GU_501750 | Cornavarrow Wind Farm | Pro-Rata |  |  | NI/2,NI/3 |  | 1 | 0 | 38.4 | wind | No | 0 | 0 | 9000 | 0
DRQ_N_Z_110 | CCG | GU_501730 | Castlecraig Wind Farm | Pro-Rata |  |  | NI/2,NI/3 |  | 1 | 0 | 25 | wind | No | 0 | 0 | 9000 | 0
DRY_I_Z_110 | IW1 | GU_401230 | Indaver - Meath Waste - Generator | Individual |  |  | ROI/1 |  | 1 | 1 | 17 | multi_fuel | Yes | -5.27 | 0 | -5.77 | -5.27
DDK_I_Z_110 | GR1 | GU_401890 | Grove Hill Windfarm | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 16.1 | wind | No | 0 | 0 | 9000 | 0
DFR_I_T_110 | HT1 | GU_405100 | Hortland Solar Farm | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 14 | solar | No | 0 | 0 | 9000 | 0
DUN_N_Z_110 | CRO | GU_501050 | Crockagarran Wind Farm | Pro-Rata |  |  | NI/4 |  | 1 | 0 | 17.5 | wind | No | 0 | 0 | 9000 | 0
DMY_I_Z_110 | BA1 | GU_406600 | Ballybane Generator Unit | Pro-Rata |  |  | ROI-W/2,ROI/1 |  | 1 | 0 | 27.95 | wind | No | 0 | 0 | 9000 | 0
DMY_I_Z_110 | BA2 | GU_401790 | Ballybane Wind Farm Phase 2 | Pro-Rata |  |  | ROI-W/2,ROI/1 |  | 1 | 0 | 13.05 | wind | No | 0 | 0 | 9000 | 0
DMY_I_Z_110 | BA3 | GU_402010 | Ballybane Wind Farm Phase 3 | Pro-Rata |  |  | ROI-W/2,ROI/1 |  | 1 | 0 | 4.45 | wind | No | 0 | 0 | 9000 | 0
DMY_I_Z_110 | KV1 | GU_401950 | Kilaveenoge 1 WF | Pro-Rata |  |  | ROI-W/2,ROI/1 |  | 1 | 0 | 24.8 | wind | No | 0 | 0 | 9000 | 0
ENN_N_Z_110 | CAL | GU_500020 | Callagheen Wind Farm | Pro-Rata |  |  | NI/2,NI/3,NI/4 |  | 1 | 0 | 16.9 | wind | No | 0 | 0 | 9000 | 0
ENN_N_Z_110 | ORA | GU_501520 | Ora More Wind Farm | Pro-Rata |  |  | NI/2,NI/3,NI/4 |  | 1 | 0 | 15 | wind | No | 0 | 0 | 9000 | 0
FIN_I_Z_110 | DG1 | GU_405860 | Huntstown TEG | Individual |  |  | ROI/1 |  | 1 | 18 | 50 | gas | Yes | 125.8 | 286.05 | 125.79 | 125.8
GAN_I_Z_110 | IA1 | GU_405840 | Gallanstown Solar | Pro-Rata |  |  | ROI-NE/2 |  | 1 | 0 | 119 | solar | No | 0 | 0 | 9000 | 0
GAN_I_Z_110 | IA2 | GU_407340 | Harlockstown Solar Farm | Pro-Rata |  |  | ROI-NE/2 |  | 1 | 0 | 31.6 | solar | No | 0 | 0 | 9000 | 0
GRH_I_Z_110 | NB1 | GU_405190 | Gillinstown Solar Farm | Pro-Rata |  |  | ROI-NE/2 |  | 1 | 0 | 95 | solar | No | 0 | 0 | 9000 | 0
GRO_I_Z_110 | CZ1 | GU_400591 | Coomacheo Generator Unit | Pro-Rata |  |  | ROI-W/2,ROI/1 |  | 1 | 0 | 59.225 | wind | No | 0 | 0 | 9000 | 0
RSK_N_Z_110 | CGR | GU_504030 | Craiggore Windfarm | Pro-Rata |  |  | NI/1,NI/4,NI/5 |  | 1 | 0 | 23.5 | wind | No | 0 | 0 | 9000 | 0
RSK_N_Z_110 | EVG | GU_504040 | Evishagaran Windfarm | Pro-Rata |  |  | NI/1,NI/4,NI/5 |  | 1 | 0 | 46.8 | wind | No | 0 | 0 | 9000 | 0
GRV_I_Z_110 | DS1 | GU_405830 | Derrysallagh Windfarm | Pro-Rata |  |  | NI/1,NI/4,NI/5,ROI-NW/3,ROI-NW/4,ROI-W/1,ROI-W/2,ROI/1 |  | 1 | 0 | 32 | wind | No | 0 | 0 | 9000 | 0
GRV_I_Z_110 | GH1 | GU_400950 | Garvagh Glebe Generator Unit | Pro-Rata |  |  | NI/1,NI/4,NI/5,ROI-NW/3,ROI-NW/4,ROI-W/1,ROI-W/2,ROI/1 |  | 1 | 0 | 26 | wind | No | 0 | 0 | 9000 | 0
GRV_I_Z_110 | GH2 | GU_400940 | Tullynahaw Generator Unit | Pro-Rata |  |  | NI/1,NI/4,NI/5,ROI-NW/3,ROI-NW/4,ROI-W/1,ROI-W/2,ROI/1 |  | 1 | 0 | 22 | wind | No | 0 | 0 | 9000 | 0
GGO_I_Z_220 | WG1 | GU_400930 | Whitegate Generator Unit | Individual |  |  | ROI/1 | S_NBMIN_ROImin,S_MWMAX_CRK_MW,S_MWMAX_STH_MW | 1 | 160 | 444 | multi_fuel | Yes | 51.72 | 85526 | 48.65 | 51.72
GAE_I_Z_110 | GLC | GU_400060 | Midas Generator Unit | Pro-Rata |  |  | ROI-W/2,ROI/1 |  | 1 | 0 | 29.8 | wind | No | 0 | 0 | 9000 | 0
GLE_I_Z_110 | MR1 | GU_403980 | Mauricetown Windfarm | Pro-Rata |  |  | ROI-W/2,ROI-SW/3a,ROI-SW/3b,ROI-SW/3c,ROI/1,ROI/1 |  | 1 | 0 | 13.8 | wind | No | 0 | 0 | 9000 | 0
GLE_I_Z_110 | TR1 | GU_404990 | Taurbeg Wind Farm | Pro-Rata |  |  | ROI-W/2,ROI-SW/3a,ROI-SW/3b,ROI-SW/3c,ROI/1,ROI/1 |  | 1 | 0 | 25.3 | wind | No | 0 | 0 | 9000 | 0
GLR_I_Z_110 | GJ1 | GU_403880 | Bunnyconnellan Windfarm | Pro-Rata |  |  | ROI-NW/3,ROI-NW/4,ROI-W/1,ROI-W/2,ROI-W/6,ROI-W/8,ROI/1 |  | 1 | 0 | 28 | wind | No | 0 | 0 | 9000 | 0
GLR_I_Z_110 | XL1 | GU_403990 | Black Lough WFPS | Pro-Rata |  |  | ROI-NW/3,ROI-NW/4,ROI-W/1,ROI-W/2,ROI-W/6,ROI-W/8,ROI/1 |  | 1 | 0 | 12.5 | wind | No | 0 | 0 | 9000 | 0
GLR_I_Z_110 | XR1 | GU_401280 | Carrowleagh Windfarm | Pro-Rata |  |  | ROI-NW/3,ROI-NW/4,ROI-W/1,ROI-W/2,ROI-W/6,ROI-W/8,ROI/1 |  | 1 | 0 | 34.15 | wind | No | 0 | 0 | 9000 | 0
GOL_I_T_110 | GO1 | GU_405880 | Barnesmore (Golagh) Windfarm | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 12 | wind | No | 0 | 0 | 9000 | 0
GWE_I_Z_110 | SD1 | GU_500740 | Slieve Divena Wind Farm | Pro-Rata |  |  | NI/2,ROI/1 |  | 1 | 0 | 30 | wind | No | 0 | 0 | 9000 | 0
GWE_I_Z_110 | SD2 | GU_501550 | Slieve Divena 2 Wind Farm | Pro-Rata |  |  | NI/2,ROI/1 |  | 1 | 0 | 18.8 | wind | No | 0 | 0 | 9000 | 0
GWE_I_Z_110 | AKN | GU_503790 | Altamuskin Wind Farm | Pro-Rata |  |  | NI/2,ROI/1 |  | 1 | 0 | 14.1 | wind | No | 0 | 0 | 9000 | 0
GWE_I_Z_110 | STS | GU_501700 | Shantavny Scotch Wind Farm | Pro-Rata |  |  | NI/2,ROI/1 |  | 1 | 0 | 16.1 | wind | No | 0 | 0 | 9000 | 0
GWE_I_Z_110 | TGS | GU_501740 | Teiges Wind Farm | Pro-Rata |  |  | NI/2,ROI/1 |  | 1 | 0 | 12.5 | wind | No | 0 | 0 | 9000 | 0
GWE_I_Z_110 | MUR | GU_504260 | Murley Mountain Windfarm | Pro-Rata |  |  | NI/2,ROI/1 |  | 1 | 0 | 21.6 | wind | No | 0 | 0 | 9000 | 0
GI_I_Z_220 | GI4 | GU_400762 | Great Island CCGT | Individual |  |  | ROI/1 | S_NBMIN_ROImin,S_MWMAX_STH_MW | 1 | 165 | 464 | multi_fuel | Yes | 79.11 | 34093.88 | 71.88 | 79.11
HN_I_Z_220 | HN2 | GU_400540 | VPL Generation Unit | Individual |  |  | ROI/1 | S_NBMIN_ROImin,S_NBMIN_DubNB2,S_NBMIN_Dub_NB,S_NBMIN_DUB_L2 | 1 | 121 | 400 | gas | Yes | 59.09 | 72518.03 | 54.19 | 59.09
HN_I_Z_220 | HNC | GU_400480 | HPC1 Generation Unit | Individual |  |  | ROI/1 | S_NBMIN_ROImin,S_NBMIN_DubNB2,S_NBMIN_Dub_NB,S_NBMIN_DUB_L1),S_NBMIN_DUB_L2 | 1 | 120 | 342 | gas | Yes | 65.1 | 96024.48 | 59.7 | 65.1
IKE_I_T_110 | MH1 | GU_401540 | Monaincha Wind Farm | Pro-Rata |  |  | ROI-W/1,ROI-W/2,ROI/1 |  | 1 | 0 | 35.95 | wind | No | 0 | 0 | 9000 | 0
INC_I_Z_220 | IL1 | GU_407560 | Grange Power IL1 Generator | Individual |  |  | ROI/1 |  | 1 | 4.6 | 18.54 | multi_fuel | Yes | 106.78 | 135.56 | 98.17 | 106.78
INC_I_Z_220 | IL2 | GU_403450 | Grange Power IL2 Generator | Individual |  |  | ROI/1 |  | 1 | 4.6 | 18.54 | multi_fuel | Yes | 106.78 | 135.56 | 98.17 | 106.78
INC_I_Z_220 | IL3 | GU_407570 | Grange Power IL3 Generator | Individual |  |  | ROI/1 |  | 1 | 4.6 | 18.54 | multi_fuel | Yes | 106.78 | 135.56 | 98.17 | 106.78
INC_I_Z_220 | IL4 | GU_407580 | Grange Power IL4 Generator | Individual |  |  | ROI/1 |  | 1 | 4.6 | 18.54 | multi_fuel | Yes | 106.78 | 135.56 | 98.17 | 106.78
INC_I_Z_220 | IL5 | GU_407590 | Grange Power IL5 Generator | Individual |  |  | ROI/1 |  | 1 | 4.6 | 18.54 | multi_fuel | Yes | 106.78 | 135.56 | 98.17 | 106.78
INC_I_Z_220 | IL6 | GU_407600 | Grange Power IL6 Generator | Individual |  |  | ROI/1 |  | 1 | 4.6 | 18.54 | multi_fuel | Yes | 106.78 | 135.56 | 98.17 | 106.78
IA_I_Z_110 | LE1 | GU_400280 | Inniscarra (Lee unit 1) Generator Unit | Individual |  |  | ROI/1 |  | 1 | 3 | 15 | hydro | Yes | 80 | 0 | 8000 | 80
IA_I_Z_110 | LE2 | GU_400281 | Lee unit 2 Generator Unit | Individual |  |  | ROI/1 |  | 1 | 1 | 4 | hydro | Yes | 80 | 0 | 8000 | 80
ISH_I_Z_220 | DB1 | GU_400500 | Dublin Bay Generator Unit | Individual |  |  | ROI/1 | S_NBMIN_ROImin,S_NBMIN_DubNB2,S_NBMIN_Dub_NB,S_NBMIN_DUB_L1),S_NBMIN_DUB_L2 | 1 | 110 | 415 | multi_fuel | Yes | 47.55 | 69518.36 | 47.53 | 47.55
ISH_I_Z_220 | IS3 | GU_403610 | Ringngsend_OCGT | Individual |  |  | ROI/1 | S_REP_ROI | 1 | 22.7 | 63.5 | multi_fuel | Yes | 110.12 | 5165.08 | 108.86 | 110.12
CUS_I_Z_110 | OE1 | GU_405140 | Cloncreen Wind Farm | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 75 | wind | No | 0 | 0 | 9000 | 0
CUS_I_Z_110 | OE2 | GU_407320 | Cloncreen Battery | Individual |  |  | ROI/1 |  | 0 | 0 | 25 | multi_fuel | Yes | 203.89 | 0 | 8.62 | 203.89
KHL_I_Z_110 | KH1 | GU_401780 | Kill Hill Wind Farm Limited | Pro-Rata |  |  | ROI-W/1,ROI-W/2,ROI/1 |  | 1 | 0 | 36 | wind | No | 0 | 0 | 9000 | 0
KMT_N_Z_110 | EGL | GU_501440 | Eglish Wind Farm | Pro-Rata |  |  | NI/2,NI/4 |  | 1 | 0 | 15 | wind | No | 0 | 0 | 9000 | 0
KMT_N_Z_110 | CKT | GU_501190 | Carrickatane Windfarm | Pro-Rata |  |  | NI/2,NI/4 |  | 1 | 0 | 20.7 | wind | No | 0 | 0 | 9000 | 0
KPG_I_Z_110 | KZ1 | GU_402300 | Kelwin Power Plant | Pro-Rata |  |  | ROI-W/2,ROI/1 |  | 1 | 0 | 37.05 | wind | No | 0 | 0 | 9000 | 0
KPG_I_Z_110 | KZ3 | GU_403000 | Kelwin 3 Diesel Unit | Individual |  |  | ROI-W/2,ROI/1 |  | 1 | 0.2 | 2 | distillate | Yes | 424.84 | 0 | 424.84 | 424.84
KPG_I_Z_110 | LM1 | GU_402210 | Leanamore Windfarm | Pro-Rata |  |  | ROI-W/2,ROI/1 |  | 1 | 0 | 18 | wind | No | 0 | 0 | 9000 | 0
KPS_N_Z_275 | KGT1 | GU_500824 | Kilroot - GT1 | Individual |  |  | NI/4 | S_MWMAX_NI_GT | 1 | 5 | 29.2 | distillate | Yes | 431.15 | 8976.52 | 425.9 | 431.15
KPS_N_Z_275 | KGT2 | GU_500825 | Kilroot - GT2 | Individual |  |  | NI/4 | S_MWMAX_NI_GT | 1 | 5 | 29.2 | distillate | Yes | 431.15 | 8976.52 | 425.9 | 431.15
KPS_N_Z_275 | KGT3 | GU_500820 | Kilroot - GT3 | Individual |  |  | NI/4 | S_MWMAX_NI_GT | 1 | 12.82 | 41.61 | distillate | Yes | 198.29 | 1258.93 | 196.54 | 198.29
KPS_N_Z_275 | KGT4 | GU_500821 | Kilroot - GT4 | Individual |  |  | NI/4 | S_MWMAX_NI_GT | 1 | 12.82 | 41.61 | distillate | Yes | 198.29 | 1258.93 | 196.54 | 198.29
KPS_N_Z_275 | KGT6 | GU_504110 | Kilroot GT6 | Individual |  |  | NI/4 | S_NBMIN_MINNIU,S_NBMIN_MINNI3 | 1 | 147 | 350 | multi_fuel | Yes | 89.08 | 142148.49 | 83.15 | 89.08
KPS_N_Z_275 | KGT7 | GU_504120 | Kilroot GT7 | Individual |  |  | NI/4 | S_NBMIN_MINNIU,S_NBMIN_MINNI3 | 1 | 147 | 350 | multi_fuel | Yes | 89.08 | 142148.49 | 83.15 | 89.08
KCR_I_Z_110 | KC1 | GU_401770 | Knockacummer Wind Farm | Pro-Rata |  |  | NI/4,ROI-W/2,ROI-SW/3a,ROI-SW/3b,ROI-SW/3c,ROI/1 |  | 1 | 0 | 100 | wind | No | 0 | 0 | 9000 | 0
KLH_I_Z_110 | KU1 | GU_403380 | Knockalough WFPS | Pro-Rata |  |  | ROI-W/1,ROI-W/2,ROI-W/3,ROI/1 |  | 1 | 0 | 33.6 | wind | No | 0 | 0 | 9000 | 0
DER_I_Z_110 | YW1 | GU_407510 | Yellow River Windfarm | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 101 | wind | No | 0 | 0 | 9000 | 0
KNY_I_Z_110 | INW1_1 | GU_401140 | Knock South Windfarm | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 2.34 | wind | No | 0 | 0 | 9000 | 0
KNY_I_Z_110 | UF1 | GU_405210 | Ardderroo Windfarm | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 91.2 | wind | No | 0 | 0 | 9000 | 0
LA_I_Z_110 | LR4 | GU_400240 | Lanesboro | Individual |  |  | ROI/1 |  | 0 | 0 | 0 | peat | Yes | 0 | 0 | 7000 | 0
LAR_N_Z_110 | BKL | GU_504200 | Ballykeel Windfarm | Pro-Rata |  |  | NI/4 |  | 1 | 0 | 16.1 | wind | No | 0 | 0 | 9000 | 0
LNA_I_Z_110 | LL1 | GU_405930 | Lenalea Windfarm | Pro-Rata |  |  | ROI-NW/1,ROI-NW/3,ROI-NW/4,ROI-W/2,ROI/1 |  | 1 | 0 | 30.1 | wind | No | 0 | 0 | 9000 | 0
LET_I_Z_110 | CAR | GU_403900 | Cark Wind Farm | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 15 | wind | No | 0 | 0 | 9000 | 0
LET_I_Z_110 | CUH | GU_400030 | Cuillagh Generator Unit | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 11.88 | wind | No | 0 | 0 | 9000 | 0
LET_I_Z_110 | BM1 | GU_404560 | Beam Hill Wind Farm | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 14 | wind | No | 0 | 0 | 9000 | 0
LET_I_Z_110 | SN1 | GU_400550 | Sorne Hill Generator Unit | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 38.9 | wind | No | 0 | 0 | 9000 | 0
LIM_N_Z_110 | ALT | GU_504060 | Altahullion (1) Wind Farm | Pro-Rata |  |  | NI/1,NI/4,NI/5 |  | 1 | 0 | 26 | wind | No | 0 | 0 | 9000 | 0
LIM_N_Z_110 | AL2 | GU_504160 | Altahullion (2) Wind Farm | Pro-Rata |  |  | NI/1,NI/4,NI/5 |  | 1 | 0 | 11.7 | wind | No | 0 | 0 | 9000 | 0
LIS_N_Z_110 | NICG2 | GU_500900 | Contour Global APTG | Individual |  |  | NI/4 |  | 1 | 0 | 3.021 | gas | Yes | 0 | 0 | 0 | 0
LIS_N_Z_110 | LRP | GU_504090 | Lough Road PV Solar Farm | Pro-Rata |  |  | NI/4 |  | 1 | 0 | 25.2 | solar | No | 0 | 0 | 9000 | 0
LIS_N_Z_110 | BDP | GU_501660 | Ballinderry Road PV Solar Farm | Pro-Rata |  |  | NI/4 |  | 1 | 0 | 16.92 | solar | No | 0 | 0 | 9000 | 0
LIS_N_Z_110 | MRP | GU_503400 | Maghaberry Road PV Solar Farm | Pro-Rata |  |  | NI/4 |  | 1 | 0 | 20.43 | solar | No | 0 | 0 | 9000 | 0
LSN_I_Z_110 | BU1 | GU_401700 | Bruckana Wind Farm Limited | Pro-Rata |  |  | ROI-W/1,ROI-W/2,ROI-W/5,ROI/1 |  | 1 | 0 | 40 | wind | No | 0 | 0 | 9000 | 0
LSN_I_Z_110 | LS1 | GU_400840 | Lisheen Windfarm Phase 1 | Pro-Rata |  |  | ROI-W/1,ROI-W/2,ROI-W/5,ROI/1 |  | 1 | 0 | 36 | wind | No | 0 | 0 | 9000 | 0
LSN_I_Z_110 | LS2 | GU_401750 | Lisheen Wind Farm 2 Ltd | Pro-Rata |  |  | ROI-W/1,ROI-W/2,ROI-W/5,ROI/1 |  | 1 | 0 | 23 | wind | No | 0 | 0 | 9000 | 0
LSN_I_Z_110 | LS3 | GU_404420 | Lisheen III Wind Farm | Pro-Rata |  |  | ROI-W/1,ROI-W/2,ROI-W/5,ROI/1 |  | 1 | 0 | 28.8 | wind | No | 0 | 0 | 9000 | 0
LSA_I_Z_110 | LA1 | GU_406610 | Drumlins Windfarm | Pro-Rata |  |  | ROI-NE/1 |  | 1 | 0 | 48.8 | wind | No | 0 | 0 | 9000 | 0
LWD_I_Z_110 | BY1 | GU_401290 | Ballycadden Wind Farm | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 15 | wind | No | 0 | 0 | 9000 | 0
LWD_I_Z_110 | BY2 | GU_401360 | Ballycadden Wind Farm Phase 2 | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 9.2 | wind | No | 0 | 0 | 9000 | 0
LWD_I_Z_110 | CK1 | GU_403390 | Castledockrell Windfarm (Gen Unit) | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 41.4 | wind | No | 0 | 0 | 9000 | 0
LWD_I_Z_110 | GT1 | GU_401340 | Gibbet Hill Windfarm | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 14.8 | wind | No | 0 | 0 | 9000 | 0
LOG_N_Z_110 | CNY | GU_501390 | Cloonty Wind Farm | Pro-Rata |  |  | NI/1,NI/4,NI/5 |  | 1 | 0 | 9.2 | wind | No | 0 | 0 | 9000 | 0
LMR_N_Z_110 | CUR | GU_501150 | Curryfree Wind Farm | Pro-Rata |  |  | NI/1,NI/4 |  | 1 | 0 | 15 | wind | No | 0 | 0 | 9000 | 0
LGT_I_Z_110 | LO1 | GU_406580 | Lysaghtstown Solar Farm | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 87 | solar | No | 0 | 0 | 9000 | 0
MAC_I_Z_110 | BN1 | GU_401150 | Bawnmore Windfarm | Pro-Rata |  |  | ROI-W/2,ROI/1 |  | 1 | 0 | 24 | wind | No | 0 | 0 | 9000 | 0
MAC_I_Z_110 | JG1 | GU_405080 | Knockglass Solar Farm | Pro-Rata |  |  | ROI-W/2,ROI/1 |  | 1 | 0 | 4 | solar | No | 0 | 0 | 9000 | 0
MKL_N_Z_110 | CRI | GU_503830 | Crighshane Wind Farm | Pro-Rata |  |  | NI/2,NI/4 |  | 1 | 0 | 32.2 | wind | No | 0 | 0 | 9000 | 0
MKL_N_Z_110 | CHU | GU_503840 | Church Hill Wind Farm | Pro-Rata |  |  | NI/2,NI/4 |  | 1 | 0 | 18.4 | wind | No | 0 | 0 | 9000 | 0
MKL_N_Z_110 | TNG | GU_503820 | Thornog Wind Farm | Pro-Rata |  |  | NI/2,NI/4 |  | 1 | 0 | 20 | wind | No | 0 | 0 | 9000 | 0
MKL_N_Z_110 | SRN | GU_503780 | Seegronan Wind Farm | Pro-Rata |  |  | NI/2,NI/4 |  | 1 | 0 | 14.1 | wind | No | 0 | 0 | 9000 | 0
MKL_N_Z_110 | TMA | GU_501500 | Tievenameenta Wind Farm | Pro-Rata |  |  | NI/2,NI/4 |  | 1 | 0 | 34.5 | wind | No | 0 | 0 | 9000 | 0
MTH_I_Z_110 | GA2 | GU_400041 | Gartnaneane Generator Unit | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 10.5 | wind | No | 0 | 0 | 9000 | 0
MTH_I_Z_110 | RR2 | GU_403970 | Raragh 2 Windfarm | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 11.5 | wind | No | 0 | 0 | 9000 | 0
MTH_I_Z_110 | VB1 | GU_405110 | Taghart Windfarm | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 23.1 | wind | No | 0 | 0 | 9000 | 0
MEE_I_Z_110 | MCT | GU_400070 | Meentycat Generator Unit | Pro-Rata |  |  | ROI-NW/2,ROI-NW/3,ROI-NW/4,ROI-W/2,ROI/1 |  | 1 | 0 | 84.96 | wind | No | 0 | 0 | 9000 | 0
MP_I_Z_380 | MP1 | GU_400270 | Moneypoint 1 Generator Unit | Individual |  |  | ROI-W/1,ROI-W/2,ROI/1 | S_NBMIN_ROImin,S_NBMIN_MP_NB | 1 | 99 | 285 | coal | Yes | 143 | 162544.66 | 143 | 143
MP_I_Z_380 | MP2 | GU_400271 | Moneypoint 2 Generator Unit | Individual |  |  | ROI-W/1,ROI-W/2,ROI/1 | S_NBMIN_ROImin,S_NBMIN_MP_NB,MP5_NB | 1 | 99 | 285 | coal | Yes | 143 | 162544.66 | 143 | 143
MP_I_Z_110 | MP9 | GU_402080 | Moneypoint Windfarm | Pro-Rata |  |  | ROI-W/1,ROI-W/2,ROI/1 |  | 1 | 0 | 17.25 | wind | No | 0 | 0 | 9000 | 0
MP_I_Z_110 | MP3 | GU_400272 | Moneypoint 3 Generator Unit | Individual |  |  | ROI-W/1,ROI-W/2,ROI/1 | S_NBMIN_ROImin,S_NBMIN_MP_NB | 1 | 99 | 285 | coal | Yes | 143 | 162544.66 | 143 | 143
MLC_I_Z_110 | MO1 | GU_401690 | Mount Lucas Wind Farm Limited | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 80 | wind | No | 0 | 0 | 9000 | 0
MRY_I_Z_110 | MB1 | GU_401930 | Mulreavy Windfarm | Pro-Rata |  |  | ROI-NW/3,ROI-NW/4,ROI-W/2,ROI/1 |  | 1 | 0 | 89.85 | wind | No | 0 | 0 | 9000 | 0
MRY_I_Z_110 | MB2 | GU_401920 | Meenadreen South 2 Windfarm | Pro-Rata |  |  | ROI-NW/3,ROI-NW/4,ROI-W/2,ROI/1 |  | 1 | 0 | 5.4 | wind | No | 0 | 0 | 9000 | 0
NEW_I_Z_110 | DZ1 | GU_407690 | Dunmurry Springs Solar Farm | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 12 | solar | No | 0 | 0 | 9000 | 0
NW_I_Z_220 | NW8 | GU_405850 | North Wall5 Generator Unit | Individual |  |  | ROI/1 |  | 1 | 17 | 200 | gas | Yes | 122.55 | 91.4 | 121.14 | 122.55
TB_I_Z_220 | TB5 | GU_406490 | Tarbert 5 TEG | Individual |  |  | ROI/1 |  | 1 | 25 | 160 | distillate | Yes | 160.08 | 520.73 | 145.57 | 160.08
OMA_N_Z_110 | LEN | GU_504050 | Lendrums Bridge (1) Wind Farm | Pro-Rata |  |  | NI/2,NI/4 |  | 1 | 0 | 7.26 | wind | No | 0 | 0 | 9000 | 0
OMA_N_Z_110 | LEN1 | GU_504070 | Lendrums Bridge (2) Wind Farm | Pro-Rata |  |  | NI/2,NI/4 |  | 1 | 0 | 5.94 | wind | No | 0 | 0 | 9000 | 0
OMA_N_Z_110 | HUN | GU_501040 | Hunter's Hill Wind Farm | Pro-Rata |  |  | NI/2,NI/4 |  | 1 | 0 | 20 | wind | No | 0 | 0 | 9000 | 0
OMA_N_Z_110 | TAP | GU_500010 | Tappaghan Wind Farm | Pro-Rata |  |  | NI/2,NI/4 |  | 1 | 0 | 28.5 | wind | No | 0 | 0 | 9000 | 0
OMA_N_Z_110 | SCR | GU_503850 | Screggagh Wind Farm | Pro-Rata |  |  | NI/2,NI/4 |  | 1 | 0 | 20 | wind | No | 0 | 0 | 9000 | 0
PA_I_Z_110 | LI1 | GU_400250 | Liffey 1 Generator Unit | Individual |  |  | ROI/1 |  | 1 | 3 | 15 | hydro | Yes | 80 | 0 | 8000 | 80
PA_I_Z_110 | LI2 | GU_400251 | Liffey 2 Generator Unit | Individual |  |  | ROI/1 |  | 1 | 3 | 15 | hydro | Yes | 80 | 0 | 8000 | 80
PA_I_Z_110 | LI3 | GU_401220 | Liffey 3 Hydro Unit | Individual |  |  | ROI/1 |  | 1 | 0 | 0.18 | hydro | Yes | 0 | 0 | 8000 | 0
PA_I_Z_110 | LI4 | GU_400252 | Liffey 4 Generator Unit | Individual |  |  | ROI/1 |  | 1 | 3.99 | 4 | hydro | Yes | 80 | 0 | 8000 | 80
PA_I_Z_110 | LI5 | GU_400260 | Liffey 5 Generator Unit | Individual |  |  | ROI/1 |  | 1 | 0.2 | 4 | hydro | Yes | 80 | 0 | 8000 | 80
PB_I_Z_220 | PB7 | GU_403620 | Poolbeg_OCGT | Individual |  |  | ROI/1 | S_REP_ROI | 1 | 22.7 | 63.5 | multi_fuel | Yes | 110.12 | 5165.08 | 108.86 | 110.12
PB_I_Z_220 | DW1 | GU_402030 | Dublin Waste to Energy | Individual |  |  | ROI/1 |  | 1 | 21.5 | 61.5 | multi_fuel | Yes | -1 | 19685.78 | -1 | -1
RSK_N_Z_110 | LMT | GU_503810 | Long Mountain Wind Farm | Pro-Rata |  |  | NI/1,NI/4,NI/5 |  | 1 | 0 | 27.6 | wind | No | 0 | 0 | 9000 | 0
RSK_N_Z_110 | AVN | GU_501620 | Altaveedan Wind Farm | Pro-Rata |  |  | NI/1,NI/4,NI/5 |  | 1 | 0 | 18 | wind | No | 0 | 0 | 9000 | 0
RSK_N_Z_110 | BNP | GU_501630 | Rasharkin PV (Bann Road PV) Solar Farm | Pro-Rata |  |  | NI/1,NI/4,NI/5 |  | 1 | 0 | 29.81 | solar | No | 0 | 0 | 9000 | 0
RAT_I_Z_110 | GW1 | GU_401090 | Grouselodge Windfarm (Gen Unit) | Pro-Rata |  |  | ROI-W/1,ROI-W/2,ROI-SW/2,ROI/1 |  | 1 | 0 | 15 | wind | No | 0 | 0 | 9000 | 0
RAT_I_Z_110 | RC1 | GU_401080 | Rathcahill West Windfarm | Pro-Rata |  |  | ROI-W/1,ROI-W/2,ROI-SW/2,ROI/1 |  | 1 | 0 | 12.5 | wind | No | 0 | 0 | 9000 | 0
RTO_I_Z_110 | RT1 | GU_407040 | Rathnaskilloge Solar Farm | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 95 | solar | No | 0 | 0 | 9000 | 0
RRU_I_Z_110 | BD1 | GU_400050 | Bindoo Generator Unit | Pro-Rata |  |  | ROI-NE/1,ROI/1 |  | 1 | 0 | 48 | wind | No | 0 | 0 | 9000 | 0
RRU_I_Z_110 | ML1 | GU_400620 | Mountain Lodge Wind Farm | Pro-Rata |  |  | ROI-NE/1,ROI/1 |  | 1 | 0 | 30.62 | wind | No | 0 | 0 | 9000 | 0
REM_I_Z_110 | KM1 | GU_401350 | Knocknagoum Windfarm Limited | Pro-Rata |  |  | ROI-W/2 |  | 1 | 0 | 44.35 | wind | No | 0 | 0 | 9000 | 0
REM_I_Z_110 | MU1 | GU_400960 | Muingnaminnane Generator Unit | Pro-Rata |  |  | ROI-W/2 |  | 1 | 0 | 14.8 | wind | No | 0 | 0 | 9000 | 0
ROP_I_Z_110 | RO1 | GU_405150 | Rosspile Solar | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 95 | solar | No | 0 | 0 | 9000 | 0
SAL_I_Z_110 | LG1 | GU_401500 | Leitir Guingaid Wind Farm phase 1 | Pro-Rata |  |  | ROI-W/1,ROI-W/2,ROI-W/3,ROI/1 |  | 1 | 0 | 40.9 | wind | No | 0 | 0 | 9000 | 0
SKL_I_Z_110 | AL1 | GU_402220 | Carrickallen Windfarm | Pro-Rata |  |  | ROI-NE/1,ROI/1 |  | 1 | 0 | 20.5 | wind | No | 0 | 0 | 9000 | 0
SH_I_Z_110 | WO4 | GU_400370 | Shannonbridge Generator Unit | Individual |  |  | ROI/1 |  | 0 | 0 | 0 | peat | Yes | 0 | 0 | 7000 | 0
SH_I_Z_110 | SQ1 | GU_406510 | Shannonbridge 1 TEG | Individual |  |  | ROI/1 |  | 1 | 16 | 260 | distillate | Yes | 132.62 | 1683.49 | 132.62 | 132.62
SHL_I_Z_220 | PBA | GU_400324 | Shellybanks PBA | Individual |  |  | ROI/1 | S_NBMIN_ROImin,S_REP_ROI,S_NBMIN_Dub_NB,S_NBMIN_DUB_L1),S_NBMIN_DUB_L2 | 1 | 120 | 240 | multi_fuel | Yes | 78.55 | 43598.24 | 77.63 | 78.55
SHL_I_Z_220 | PBB | GU_400325 | Shellybanks PBB | Individual |  |  | ROI/1 | S_NBMIN_ROImin,S_REP_ROI,S_NBMIN_Dub_NB,S_NBMIN_DUB_L1),S_NBMIN_DUB_L2 | 1 | 120 | 236 | multi_fuel | Yes | 78.54 | 43598.24 | 77.64 | 78.54
KMT_N_Z_110 | SK1 | GU_501160 | Slieve Kirk Wind Farm | Pro-Rata |  |  | NI/2,NI/4 |  | 1 | 0 | 73.6 | wind | No | 0 | 0 | 9000 | 0
DAL_I_T_110 | DN1 | GU_406620 | Derrinlough Windfarm | Pro-Rata |  |  | ROI-W/1,ROI-W/2,ROI/1 |  | 1 | 0 | 105 | wind | No | 0 | 0 | 9000 | 0
TAN_N_Z_110 | CMN | GU_504340 | Carnmeen Generator | Individual |  |  | NI/4 | S_MWMAX_NI_GT | 1 | 1 | 20 | multi_fuel | Yes | 422.44 | 23496.28 | 331.49 | 422.44
TAW_I_Z_110 | KF1 | GU_403750 | Killala Windfarm | Pro-Rata |  |  | ROI-NW/3,ROI-NW/4,ROI-W/1,ROI-W/2,ROI-W/6,ROI-W/7,ROI-W/8,ROI/1 |  | 1 | 0 | 19.2 | wind | No | 0 | 0 | 9000 | 0
TAW_I_Z_110 | TP1 | GU_400780 | Tawnaghmore Peaking 1 Generator Unit | Individual |  |  | ROI-NW/3,ROI-NW/4,ROI-W/1,ROI-W/2,ROI-W/6,ROI-W/7,ROI-W/8,ROI/1 | S_REP_ROI | 1 | 5 | 52 | distillate | Yes | 213.18 | 879.73 | 193.76 | 213.18
TAW_I_Z_110 | TP3 | GU_400781 | Tawnaghmore Peaking 3 Generator Unit | Individual |  |  | ROI-NW/3,ROI-NW/4,ROI-W/1,ROI-W/2,ROI-W/6,ROI-W/7,ROI-W/8,ROI/1 | S_REP_ROI | 1 | 5 | 52 | distillate | Yes | 213.18 | 879.73 | 193.76 | 213.18
THU_I_Z_110 | AC1 | GU_401670 | Cnoc Windfarms | Pro-Rata |  |  | ROI-W/1,ROI-W/2,ROI/1 |  | 1 | 0 | 11.5 | wind | No | 0 | 0 | 9000 | 0
THU_I_Z_110 | BS1 | GU_404580 | Ballybay Wind Farm | Pro-Rata |  |  | ROI-W/1,ROI-W/2,ROI/1 |  | 1 | 0 | 13.8 | wind | No | 0 | 0 | 9000 | 0
TIV_I_Z_110 | YC2 | GU_403840 | Cronalaght 2 | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 17.25 | wind | No | 0 | 0 | 9000 | 0
TEN_I_Z_110 | TE1 | GU_406590 | Timahoe North Solar Farm | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 70 | wind | No | 0 | 0 | 9000 | 0
TRL_I_Z_110 | BCW | GU_401000 | Ballincollig Hill Generator Unit | Pro-Rata |  |  | ROI-W/2,ROI/1 |  | 1 | 0 | 13.3 | wind | No | 0 | 0 | 9000 | 0
TRL_I_Z_110 | TUR | GU_403830 | Tursillagh Windfarm | Pro-Rata |  |  | ROI-W/2,ROI/1 |  | 1 | 0 | 15.18 | wind | No | 0 | 0 | 9000 | 0
TRE_N_Z_110 | GFB | GU_503800 | Gortfinbar Wind Farm | Pro-Rata |  |  | NI/2,NI/4 |  | 1 | 0 | 15 | wind | No | 0 | 0 | 9000 | 0
TRE_N_Z_110 | CNR | GU_503940 | Cregganconroe Wind Farm | Pro-Rata |  |  | NI/2,NI/4 |  | 1 | 0 | 13.8 | wind | No | 0 | 0 | 9000 | 0
TRE_N_Z_110 | INT | GU_503930 | Inishative Wind Farm | Pro-Rata |  |  | NI/2,NI/4 |  | 1 | 0 | 13.8 | wind | No | 0 | 0 | 9000 | 0
TRE_N_Z_110 | CDN | GU_501710 | Crockandun Wind Farm | Pro-Rata |  |  | NI/2,NI/4 |  | 1 | 0 | 15 | wind | No | 0 | 0 | 9000 | 0
TRE_N_Z_110 | CKD | GU_501430 | Crockdun Wind Farm | Pro-Rata |  |  | NI/2,NI/4 |  | 1 | 0 | 12.5 | wind | No | 0 | 0 | 9000 | 0
TRI_I_Z_110 | KW2 | GU_404290 | Knockawarriga 2 Windfarm | Pro-Rata |  |  | ROI-W/2,ROI/1 |  | 1 | 0 | 6.6 | wind | No | 0 | 0 | 9000 | 0
TTU_I_Z_110 | TL1 | GU_406470 | Tullabeg Solar Farm | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 50 | solar | No | 0 | 0 | 9000 | 0
TBK_I_T_110 | MMR | GU_400970 | Moanmore Windfarm Generator Unit | Pro-Rata |  |  | ROI-W/1,ROI-W/2,ROI/1 |  | 1 | 0 | 12.6 | wind | No | 0 | 0 | 9000 | 0
TBK_I_T_110 | TK1 | GU_402050 | Tullabrack Windfarm | Pro-Rata |  |  | ROI-W/1,ROI-W/2,ROI/1 |  | 1 | 0 | 13.8 | wind | No | 0 | 0 | 9000 | 0
TH_I_Z_220 | TH1 | GU_400360 | Turlough Hill 1 Generator Unit | Individual |  |  | ROI/1 |  | 1 | 5 | 73 | pump_storage | Yes | 0 | 0 | -3.19 | 0
TH_I_Z_220 | TH2 | GU_400361 | Turlough Hill 2 Generator Unit | Individual |  |  | ROI/1 |  | 1 | 5 | 73 | pump_storage | Yes | 0 | 0 | -3.19 | 0
TH_I_Z_220 | TH3 | GU_400362 | Turlough Hill 3 Generator Unit | Individual |  |  | ROI/1 |  | 1 | 5 | 73 | pump_storage | Yes | 0 | 0 | -3.19 | 0
TH_I_Z_220 | TH4 | GU_400363 | Turlough Hill 4 Generator Unit | Individual |  |  | ROI/1 |  | 1 | 5 | 73 | pump_storage | Yes | 0 | 0 | -3.19 | 0
TYN_I_Z_220 | TYC | GU_400530 | Tynagh Generator Unit | Individual |  |  | ROI/1 | S_NBMIN_ROImin,S_NBMIN_MP_NB | 1 | 194 | 404 | gas | Yes | 79.1 | 98038.7 | 26.6 | 79.1
UGL_I_Z_110 | SO1 | GU_401990 | Seecon Windfarm | Pro-Rata |  |  | ROI-W/1,ROI-W/2,ROI-W/3,ROI/1 |  | 1 | 0 | 105 | wind | No | 0 | 0 | 9000 | 0
UGL_I_Z_110 | UG1 | GU_401960 | Uggool Wind Farm | Pro-Rata |  |  | ROI-W/1,ROI-W/2,ROI-W/3,ROI/1 |  | 1 | 0 | 64 | wind | No | 0 | 0 | 9000 | 0
WAT_I_Z_110 | BX1 | GU_401710 | Ballymartin Wind Farm Phase 1 | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 6 | wind | No | 0 | 0 | 9000 | 0
WAT_I_Z_110 | BX2 | GU_401760 | Ballymartin Wind Farm Phase 2 | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 9 | wind | No | 0 | 0 | 9000 | 0
WEX_I_Z_110 | CNS | GU_400470 | Carnsore Point Generator Unit | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 11.9 | wind | No | 0 | 0 | 9000 | 0
WEX_I_Z_110 | RF1 | GU_400080 | Richfield Generator Unit | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 27 | wind | No | 0 | 0 | 9000 | 0
WHO_I_Z_110 | WS1 | GU_401680 | Woodhouse Wind Farm | Pro-Rata |  |  | ROI/1 |  | 1 | 0 | 20 | wind | No | 0 | 0 | 9000 | 0
Note on J4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not included in model - interconnector under construction.
Note on J40: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not included in model - BESS
Note on J113: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not included in model - BESS
Note on J114: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not included in model - BESS
Note on J170: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not included in model - BESS

## ts_PGMINGEN
timestep | EWIC | DV1 | SB1 | KD1 | RD1 | OY1 | OY2 | KW1 | TN2 | AT1 | AT2 | AT4 | AD2 | MYM | SL2 | CBY | AA1 | AA2 | AA3 | AA4 | ABK | RL1 | YR1 | AH1 | XT1 | SK3 | SK4 | BGT1 | BGT2 | B10 | B31 | B32 | M | BW1 | HS1 | RHY | EGH | BF1 | SS1 | CU1 | MC1 | YV2 | NA1 | BG1 | BG2 | ES1 | CD1 | QA1 | BT1 | BT2 | LY1 | SF1 | SF2 | BJ1 | BKY | YM1 | GE1 | CNH | LE3 | XA1 | MX1 | AS1 | ER3 | ER4 | CP1 | CP3 | GM1 | GU1 | GY1 | KQ1 | PO1 | CJ1 | CJ2 | ER1 | ER2 | CL1 | DA1 | DA2 | KI1 | OA1 | GAR | GRU | DMR | DBG | LPS | MBY | CGT8 | C30 | CG1 | CG2 | CG3 | YT1 | GD1 | DL1 | DL2 | OG1 | ST1 | ST2 | TM2 | TM3 | FG2 | KG2 | KGM | ED1 | ED3 | ED5 | MM1 | QB1 | DY1 | NC1 | RP1 | RP2 | DR1 | CNV | CCG | IW1 | GR1 | HT1 | CRO | BA1 | BA2 | BA3 | KV1 | CAL | ORA | DG1 | IA1 | IA2 | NB1 | CZ1 | CGR | EVG | DS1 | GH1 | GH2 | WG1 | GLC | MR1 | TR1 | GJ1 | XL1 | XR1 | GO1 | SD1 | SD2 | AKN | STS | TGS | MUR | GI4 | HN2 | HNC | MH1 | IL1 | IL2 | IL3 | IL4 | IL5 | IL6 | LE1 | LE2 | DB1 | IS3 | OE1 | KH1 | EGL | CKT | KZ1 | KZ3 | LM1 | KGT1 | KGT2 | KGT3 | KGT4 | KGT6 | KGT7 | KC1 | KU1 | YW1 | INW1_1 | UF1 | BKL | LL1 | CAR | CUH | BM1 | SN1 | ALT | AL2 | NICG2 | LRP | BDP | MRP | BU1 | LS1 | LS2 | LS3 | LA1 | BY1 | BY2 | CK1 | GT1 | CNY | CUR | LO1 | BN1 | JG1 | CRI | CHU | TNG | SRN | TMA | GA2 | RR2 | VB1 | MCT | MP1 | MP2 | MP9 | MP3 | MO1 | MB1 | MB2 | DZ1 | NW8 | TB5 | LEN | LEN1 | HUN | TAP | SCR | LI1 | LI2 | LI3 | LI4 | LI5 | PB7 | DW1 | LMT | AVN | BNP | GW1 | RC1 | RT1 | BD1 | ML1 | KM1 | MU1 | RO1 | LG1 | AL1 | SQ1 | PBA | PBB | SK1 | DN1 | CMN | KF1 | TP1 | TP3 | AC1 | BS1 | YC2 | TE1 | BCW | TUR | GFB | CNR | INT | CDN | CKD | KW2 | TL1 | MMR | TK1 | TH1 | TH2 | TH3 | TH4 | TYC | SO1 | UG1 | BX1 | BX2 | CNS | RF1 | WS1
t-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## ts_PGLB
timestep | EWIC | DV1 | SB1 | KD1 | RD1 | OY1 | OY2 | KW1 | TN2 | AT1 | AT2 | AT4 | AD2 | MYM | SL2 | CBY | AA1 | AA2 | AA3 | AA4 | ABK | RL1 | YR1 | AH1 | XT1 | SK3 | SK4 | BGT1 | BGT2 | B10 | B31 | B32 | M | BW1 | HS1 | RHY | EGH | BF1 | SS1 | CU1 | MC1 | YV2 | NA1 | BG1 | BG2 | ES1 | CD1 | QA1 | BT1 | BT2 | LY1 | SF1 | SF2 | BJ1 | BKY | YM1 | GE1 | CNH | LE3 | XA1 | MX1 | AS1 | ER3 | ER4 | CP1 | CP3 | GM1 | GU1 | GY1 | KQ1 | PO1 | CJ1 | CJ2 | ER1 | ER2 | CL1 | DA1 | DA2 | KI1 | OA1 | GAR | GRU | DMR | DBG | LPS | MBY | CGT8 | C30 | CG1 | CG2 | CG3 | YT1 | GD1 | DL1 | DL2 | OG1 | ST1 | ST2 | TM2 | TM3 | FG2 | KG2 | KGM | ED1 | ED3 | ED5 | MM1 | QB1 | DY1 | NC1 | RP1 | RP2 | DR1 | CNV | CCG | IW1 | GR1 | HT1 | CRO | BA1 | BA2 | BA3 | KV1 | CAL | ORA | DG1 | IA1 | IA2 | NB1 | CZ1 | CGR | EVG | DS1 | GH1 | GH2 | WG1 | GLC | MR1 | TR1 | GJ1 | XL1 | XR1 | GO1 | SD1 | SD2 | AKN | STS | TGS | MUR | GI4 | HN2 | HNC | MH1 | IL1 | IL2 | IL3 | IL4 | IL5 | IL6 | LE1 | LE2 | DB1 | IS3 | OE1 | KH1 | EGL | CKT | KZ1 | KZ3 | LM1 | KGT1 | KGT2 | KGT3 | KGT4 | KGT6 | KGT7 | KC1 | KU1 | YW1 | INW1_1 | UF1 | BKL | LL1 | CAR | CUH | BM1 | SN1 | ALT | AL2 | NICG2 | LRP | BDP | MRP | BU1 | LS1 | LS2 | LS3 | LA1 | BY1 | BY2 | CK1 | GT1 | CNY | CUR | LO1 | BN1 | JG1 | CRI | CHU | TNG | SRN | TMA | GA2 | RR2 | VB1 | MCT | MP1 | MP2 | MP9 | MP3 | MO1 | MB1 | MB2 | DZ1 | NW8 | TB5 | LEN | LEN1 | HUN | TAP | SCR | LI1 | LI2 | LI3 | LI4 | LI5 | PB7 | DW1 | LMT | AVN | BNP | GW1 | RC1 | RT1 | BD1 | ML1 | KM1 | MU1 | RO1 | LG1 | AL1 | SQ1 | PBA | PBB | SK1 | DN1 | CMN | KF1 | TP1 | TP3 | AC1 | BS1 | YC2 | TE1 | BCW | TUR | GFB | CNR | INT | CDN | CKD | KW2 | TL1 | MMR | TK1 | TH1 | TH2 | TH3 | TH4 | TYC | SO1 | UG1 | BX1 | BX2 | CNS | RF1 | WS1
t-1 | -504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 15 | 120 | 0 | 0 | 0 | 11.9 | 11.9 | 11.9 | 11.9 | 0 | 0 | 0 | 0 | 0 | 40 | 40 | 8 | 8 | 63 | 113 | 113 | -441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.74 | 0 | 211 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.5 | 0 | 0 | 41.15 | 20 | 20 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 121 | 120 | 0 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 4.6 | 3 | 1 | 110 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 5 | 5 | 12.82 | 12.82 | 147 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 99 | 0 | 99 | 0 | 0 | 0 | 0 | 17 | 25 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 0 | 3.99 | 0.2 | 22.7 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 120 | 120 | 0 | 0 | 1 | 0 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 5 | 5 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## ts_PGUB
timestep | EWIC | DV1 | SB1 | KD1 | RD1 | OY1 | OY2 | KW1 | TN2 | AT1 | AT2 | AT4 | AD2 | MYM | SL2 | CBY | AA1 | AA2 | AA3 | AA4 | ABK | RL1 | YR1 | AH1 | XT1 | SK3 | SK4 | BGT1 | BGT2 | B10 | B31 | B32 | M | BW1 | HS1 | RHY | EGH | BF1 | SS1 | CU1 | MC1 | YV2 | NA1 | BG1 | BG2 | ES1 | CD1 | QA1 | BT1 | BT2 | LY1 | SF1 | SF2 | BJ1 | BKY | YM1 | GE1 | CNH | LE3 | XA1 | MX1 | AS1 | ER3 | ER4 | CP1 | CP3 | GM1 | GU1 | GY1 | KQ1 | PO1 | CJ1 | CJ2 | ER1 | ER2 | CL1 | DA1 | DA2 | KI1 | OA1 | GAR | GRU | DMR | DBG | LPS | MBY | CGT8 | C30 | CG1 | CG2 | CG3 | YT1 | GD1 | DL1 | DL2 | OG1 | ST1 | ST2 | TM2 | TM3 | FG2 | KG2 | KGM | ED1 | ED3 | ED5 | MM1 | QB1 | DY1 | NC1 | RP1 | RP2 | DR1 | CNV | CCG | IW1 | GR1 | HT1 | CRO | BA1 | BA2 | BA3 | KV1 | CAL | ORA | DG1 | IA1 | IA2 | NB1 | CZ1 | CGR | EVG | DS1 | GH1 | GH2 | WG1 | GLC | MR1 | TR1 | GJ1 | XL1 | XR1 | GO1 | SD1 | SD2 | AKN | STS | TGS | MUR | GI4 | HN2 | HNC | MH1 | IL1 | IL2 | IL3 | IL4 | IL5 | IL6 | LE1 | LE2 | DB1 | IS3 | OE1 | KH1 | EGL | CKT | KZ1 | KZ3 | LM1 | KGT1 | KGT2 | KGT3 | KGT4 | KGT6 | KGT7 | KC1 | KU1 | YW1 | INW1_1 | UF1 | BKL | LL1 | CAR | CUH | BM1 | SN1 | ALT | AL2 | NICG2 | LRP | BDP | MRP | BU1 | LS1 | LS2 | LS3 | LA1 | BY1 | BY2 | CK1 | GT1 | CNY | CUR | LO1 | BN1 | JG1 | CRI | CHU | TNG | SRN | TMA | GA2 | RR2 | VB1 | MCT | MP1 | MP2 | MP9 | MP3 | MO1 | MB1 | MB2 | DZ1 | NW8 | TB5 | LEN | LEN1 | HUN | TAP | SCR | LI1 | LI2 | LI3 | LI4 | LI5 | PB7 | DW1 | LMT | AVN | BNP | GW1 | RC1 | RT1 | BD1 | ML1 | KM1 | MU1 | RO1 | LG1 | AL1 | SQ1 | PBA | PBB | SK1 | DN1 | CMN | KF1 | TP1 | TP3 | AC1 | BS1 | YC2 | TE1 | BCW | TUR | GFB | CNR | INT | CDN | CKD | KW2 | TL1 | MMR | TK1 | TH1 | TH2 | TH3 | TH4 | TYC | SO1 | UG1 | BX1 | BX2 | CNS | RF1 | WS1
t-1 | 526 | 27 | 58 | 27 | 45 | 89 | 83 | 22.5 | 17.2 | 90 | 90 | 90 | 449 | 15 | 54 | 5.4 | 21 | 22 | 19 | 24 | 25.6 | 35.2 | 18 | 34.35 | 24 | 83 | 83 | 58 | 58 | 101 | 247 | 247 | 410 | 42 | 10 | 21.15 | 23 | 32.4 | 16.8 | 4.3 | 11.9 | 10.8 | 60 | 57 | 65.7 | 23.2 | 20 | 56.4 | 20 | 12 | 13.4 | 24 | 8.55 | 36.98 | 47.5 | 21 | 20 | 13.8 | 8 | 54.3 | 18.7 | 17.5 | 22.5 | 22.5 | 52 | 14.132 | 38 | 32.5 | 33 | 18.3 | 33.1 | 37.85 | 14 | 10 | 10 | 46 | 20 | 12 | 11.5 | 90 | 15 | 25 | 21 | 42 | 17.6 | 12 | 425 | 53 | 42.5 | 8.5 | 30 | 42.64 | 114.2 | 36 | 54 | 17.5 | 34.5 | 4.8 | 10.3 | 13.58 | 63.5 | 11.05 | 25 | 118 | 58 | 58 | 40.8 | 85 | 59.5 | 34 | 52 | 52 | 28.5 | 38.4 | 25 | 17 | 16.1 | 14 | 17.5 | 27.95 | 13.05 | 4.45 | 24.8 | 16.9 | 15 | 50 | 119 | 31.6 | 95 | 59.225 | 23.5 | 46.8 | 32 | 26 | 22 | 444 | 29.8 | 13.8 | 25.3 | 28 | 12.5 | 34.15 | 12 | 30 | 18.8 | 14.1 | 16.1 | 12.5 | 21.6 | 464 | 400 | 342 | 35.95 | 18.54 | 18.54 | 18.54 | 18.54 | 18.54 | 18.54 | 15 | 4 | 415 | 63.5 | 75 | 36 | 15 | 20.7 | 37.05 | 2 | 18 | 29.2 | 29.2 | 41.61 | 41.61 | 350 | 350 | 100 | 33.6 | 101 | 2.34 | 91.2 | 16.1 | 30.1 | 15 | 11.88 | 14 | 38.9 | 26 | 11.7 | 3.021 | 25.2 | 16.92 | 20.43 | 40 | 36 | 23 | 28.8 | 48.8 | 15 | 9.2 | 41.4 | 14.8 | 9.2 | 15 | 87 | 24 | 4 | 32.2 | 18.4 | 20 | 14.1 | 34.5 | 10.5 | 11.5 | 23.1 | 84.96 | 285 | 285 | 17.25 | 285 | 80 | 89.85 | 5.4 | 12 | 200 | 160 | 7.26 | 5.94 | 20 | 28.5 | 20 | 15 | 15 | 0.18 | 4 | 4 | 63.5 | 61.5 | 27.6 | 18 | 29.81 | 15 | 12.5 | 95 | 48 | 30.62 | 44.35 | 14.8 | 95 | 40.9 | 20.5 | 260 | 240 | 236 | 73.6 | 105 | 20 | 19.2 | 52 | 52 | 11.5 | 13.8 | 17.25 | 70 | 13.3 | 15.18 | 15 | 13.8 | 13.8 | 15 | 12.5 | 6.6 | 50 | 12.6 | 13.8 | 73 | 73 | 73 | 73 | 404 | 105 | 64 | 6 | 9 | 11.9 | 27 | 20

## ts_bid
timestep | EWIC | DV1 | SB1 | KD1 | RD1 | OY1 | OY2 | KW1 | TN2 | AT1 | AT2 | AT4 | AD2 | MYM | SL2 | CBY | AA1 | AA2 | AA3 | AA4 | ABK | RL1 | YR1 | AH1 | XT1 | SK3 | SK4 | BGT1 | BGT2 | B10 | B31 | B32 | M | BW1 | HS1 | RHY | EGH | BF1 | SS1 | CU1 | MC1 | YV2 | NA1 | BG1 | BG2 | ES1 | CD1 | QA1 | BT1 | BT2 | LY1 | SF1 | SF2 | BJ1 | BKY | YM1 | GE1 | CNH | LE3 | XA1 | MX1 | AS1 | ER3 | ER4 | CP1 | CP3 | GM1 | GU1 | GY1 | KQ1 | PO1 | CJ1 | CJ2 | ER1 | ER2 | CL1 | DA1 | DA2 | KI1 | OA1 | GAR | GRU | DMR | DBG | LPS | MBY | CGT8 | C30 | CG1 | CG2 | CG3 | YT1 | GD1 | DL1 | DL2 | OG1 | ST1 | ST2 | TM2 | TM3 | FG2 | KG2 | KGM | ED1 | ED3 | ED5 | MM1 | QB1 | DY1 | NC1 | RP1 | RP2 | DR1 | CNV | CCG | IW1 | GR1 | HT1 | CRO | BA1 | BA2 | BA3 | KV1 | CAL | ORA | DG1 | IA1 | IA2 | NB1 | CZ1 | CGR | EVG | DS1 | GH1 | GH2 | WG1 | GLC | MR1 | TR1 | GJ1 | XL1 | XR1 | GO1 | SD1 | SD2 | AKN | STS | TGS | MUR | GI4 | HN2 | HNC | MH1 | IL1 | IL2 | IL3 | IL4 | IL5 | IL6 | LE1 | LE2 | DB1 | IS3 | OE1 | KH1 | EGL | CKT | KZ1 | KZ3 | LM1 | KGT1 | KGT2 | KGT3 | KGT4 | KGT6 | KGT7 | KC1 | KU1 | YW1 | INW1_1 | UF1 | BKL | LL1 | CAR | CUH | BM1 | SN1 | ALT | AL2 | NICG2 | LRP | BDP | MRP | BU1 | LS1 | LS2 | LS3 | LA1 | BY1 | BY2 | CK1 | GT1 | CNY | CUR | LO1 | BN1 | JG1 | CRI | CHU | TNG | SRN | TMA | GA2 | RR2 | VB1 | MCT | MP1 | MP2 | MP9 | MP3 | MO1 | MB1 | MB2 | DZ1 | NW8 | TB5 | LEN | LEN1 | HUN | TAP | SCR | LI1 | LI2 | LI3 | LI4 | LI5 | PB7 | DW1 | LMT | AVN | BNP | GW1 | RC1 | RT1 | BD1 | ML1 | KM1 | MU1 | RO1 | LG1 | AL1 | SQ1 | PBA | PBB | SK1 | DN1 | CMN | KF1 | TP1 | TP3 | AC1 | BS1 | YC2 | TE1 | BCW | TUR | GFB | CNR | INT | CDN | CKD | KW2 | TL1 | MMR | TK1 | TH1 | TH2 | TH3 | TH4 | TYC | SO1 | UG1 | BX1 | BX2 | CNS | RF1 | WS1
t-1 | 10000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 108.19 | 108.18 | 108.17 | 40.96 | 9000 | 9000 | 9000 | 8000 | 8000 | 8000 | 8000 | 9000 | 9000 | 9000 | 9000 | 9000 | -1000 | -1000 | 246.74 | 246.74 | 79.19 | 75.91 | 75.91 | 10000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 8000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 8000 | 9000 | 9000 | 9000 | 8000 | 8000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 8000 | 8000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 8000 | 9000 | 51.59 | 206.04 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 111.57 | 9000 | 9000 | 7000 | 506.96 | 506.95 | 9000 | 9000 | 9000 | 9000 | 190.97 | 190.97 | 9000 | 9000 | 9000 | -5.77 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 125.79 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 48.65 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 71.88 | 54.19 | 59.7 | 9000 | 98.17 | 98.17 | 98.17 | 98.17 | 98.17 | 98.17 | 8000 | 8000 | 47.53 | 108.86 | 9000 | 9000 | 9000 | 9000 | 9000 | 424.84 | 9000 | 425.9 | 425.9 | 196.54 | 196.54 | 83.15 | 83.15 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 0 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 143 | 143 | 9000 | 143 | 9000 | 9000 | 9000 | 9000 | 121.14 | 145.57 | 9000 | 9000 | 9000 | 9000 | 9000 | 8000 | 8000 | 8000 | 8000 | 8000 | 108.86 | -1 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 132.62 | 77.63 | 77.64 | 9000 | 9000 | 331.49 | 9000 | 193.76 | 193.76 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | -3.19 | -3.19 | -3.19 | -3.19 | 26.6 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000

## baseMVA
baseMVA
100